## NPCC_N-1_VOLTAGE_SUM
BUS | VCONT | VINIT | CONTINGENCY | COMMENTS
100121 MASON 1 115.00 | 1.0745 | 1.0319 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100122 MAINE YANKEE115.00 | 1.0708 | 1.0307 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100161 NEWCASTLE 115.00 | 1.0586 | 1.0252 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100190 MASON 2 115.00 | 1.0747 | 1.0321 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100192 MASON 5 115.00 | 1.0746 | 1.0319 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100199 SECT 207A TP115.00 | 1.0708 | 1.0307 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100309 MASON_C 115.00 | 1.0747 | 1.0321 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100315 MASON_C1 115.00 | 1.0747 | 1.0321 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
100316 MASON_C2 115.00 | 1.0747 | 1.0321 | OPEN LINE FROM BUS 100091 [MASON 345.00] TO BUS 100192 [MASON 5 115.00] CKT 1
104111 MERRIMACK 230.00 | 1.0618 | 1.0459 | OPEN LINE FROM BUS 104113 [NU_A253_NGR 230.00] TO BUS 106011 [DUNBARTAN TP230.00] CKT 1
104113 NU_A253_NGR 230.00 | 1.062 | 1.041 | OPEN LINE FROM BUS 104113 [NU_A253_NGR 230.00] TO BUS 106011 [DUNBARTAN TP230.00] CKT 1
106011 DUNBARTAN TP230.00 | 1.0527 | 1.041 | OPEN LINE FROM BUS 106011 [DUNBARTAN TP230.00] TO BUS 106013 [N.LITCHFLD2 230.00] CKT 1
110789 WALTHAM 230.00 | 1.0579 | 1.0214 | OPEN LINE FROM BUS 110789 [WALTHAM 230.00] TO BUS 110810 [WALTHAM PS 115.00] CKT 1
110793 W MEDWAY B 230.00 | 1.0558 | 1.0399 | OPEN LINE FROM BUS 110795 [FRAMINGHAM 230.00] TO BUS 110870 [FRAMINGHAM 115.00] CKT 1
110794 W MEDWAY A 230.00 | 1.0565 | 1.0449 | OPEN LINE FROM BUS 110789 [WALTHAM 230.00] TO BUS 110810 [WALTHAM PS 115.00] CKT 1
110795 FRAMINGHAM 230.00 | 1.0561 | 1.0253 | OPEN LINE FROM BUS 110795 [FRAMINGHAM 230.00] TO BUS 110870 [FRAMINGHAM 115.00] CKT 1
111134 W BARNSTABLE345.00 | 1.1279 | 1.0456 | OPEN LINE FROM BUS 111133 [CARVER 345.00] TO BUS 111134 [W BARNSTABLE345.00] CKT 1
111135 W BARNSTABLE115.00 | 1.1286 | 1.0742 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111202 BARNSTABLE 115.00 | 1.1384 | 1.0887 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111203 DENNIS_TP118115.00 | 1.1432 | 1.091 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111204 FALMOUTH 115115.00 | 1.0769 | 1.0548 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111205 FALMOUTH 107115.00 | 1.075 | 1.0529 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111206 FALMOUTH TAP115.00 | 1.0799 | 1.0579 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111207 HARWICH_T119115.00 | 1.1311 | 1.0803 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111208 HARWICH ASEA115.00 | 1.1288 | 1.0777 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111209 HATCHVILLE 115.00 | 1.0886 | 1.0616 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111210 HYANNIS_J124115.00 | 1.1404 | 1.0906 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111211 HYANNIS_J123115.00 | 1.1378 | 1.0881 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111213 ORLEANS 119 115.00 | 1.1265 | 1.075 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111214 OTIS 115.00 | 1.0544 | 1.0446 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111216 WELLFLEET 115.00 | 1.1243 | 1.0687 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111218 HARWICH MCGR115.00 | 1.1491 | 1.0961 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111221 ORLEANS 118 115.00 | 1.1381 | 1.0844 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111245 SANDWICH 122115.00 | 1.0785 | 1.0582 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111246 OAK ST 122 115.00 | 1.1097 | 1.074 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111282 HARWICH 118 115.00 | 1.1491 | 1.0961 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111283 HARWICH 119 115.00 | 1.1288 | 1.0777 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111284 W BARNSTBL R115.00 | 1.1286 | 1.0742 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111285 CAPE WD_PCC1115.00 | 1.1465 | 1.0965 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111303 CAPE WD_PCC3115.00 | 1.1465 | 1.0965 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111321 CAPE WD_R12 115.00 | 1.1384 | 1.0887 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111322 CAPE WD_FTR1115.00 | 1.1384 | 1.0887 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111323 CAPE WD_ESP1115.00 | 1.1465 | 1.0965 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111324 CAPE WD_ESP2115.00 | 1.1465 | 1.0965 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111325 CAPE WD_R34 115.00 | 1.1384 | 1.0887 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111326 CAPE WD_FTR2115.00 | 1.1384 | 1.0887 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111380 CAPE WD_UW1B115.00 | 1.1437 | 1.0938 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111381 CAPE WD_UW1A115.00 | 1.1437 | 1.0938 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111382 CAPE WD_UW2B115.00 | 1.1437 | 1.0938 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111383 CAPE WD_UW2A115.00 | 1.1437 | 1.0938 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111400 BARNSTABLE_C115.00 | 1.1384 | 1.0887 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111401 FALMOUTH T_C115.00 | 1.0799 | 1.0579 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111402 HYANNIS J_C 115.00 | 1.1404 | 1.0906 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111403 MASHPEE_C 115.00 | 1.1083 | 1.0716 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111404 HARWICH_C 115.00 | 1.1491 | 1.0961 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
111405 ORLEANS_C 115.00 | 1.1381 | 1.0844 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
115969 MERCHNTS WAY115.00 | 1.1384 | 1.0886 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
115970 LOTHROP AVE 115.00 | 1.1491 | 1.0961 | OPEN LINE FROM BUS 111134 [W BARNSTABLE345.00] TO BUS 111135 [W BARNSTABLE115.00] CKT 1
119376 NU_387_UI 345.00 | 1.0621 | 1.043 | OPEN LINE FROM BUS 119142 [SCOVILLE RCK345.00] TO BUS 119376 [NU_387_UI 345.00] CKT 1
123636 ESHORE 8X 345.00 | 1.0659 | 1.0457 | OPEN LINE FROM BUS 123638 [ESHORE TELEM345.00] TO BUS 123654 [E SHORE_TAP 345.00] CKT 1
123637 ESHORE 9X 345.00 | 1.0659 | 1.0457 | OPEN LINE FROM BUS 123638 [ESHORE TELEM345.00] TO BUS 123654 [E SHORE_TAP 345.00] CKT 1
123638 ESHORE TELEM345.00 | 1.0659 | 1.0457 | OPEN LINE FROM BUS 123638 [ESHORE TELEM345.00] TO BUS 123654 [E SHORE_TAP 345.00] CKT 1
123654 E SHORE_TAP 345.00 | 1.062 | 1.0457 | OPEN LINE FROM BUS 119142 [SCOVILLE RCK345.00] TO BUS 119376 [NU_387_UI 345.00] CKT 1
123783 HALVARSSON 345.00 | 1.062 | 1.0457 | OPEN LINE FROM BUS 119142 [SCOVILLE RCK345.00] TO BUS 119376 [NU_387_UI 345.00] CKT 1
125040 N.CAT. 1 115.00 | 1.0551 | 1.0508 | SB:MARC_765_7402 TRIP BRANCH FROM BUS 147828 [MASS 765 765.00] TO BUS 180819 [CHA-NY 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147828 [MASS 765 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 2 | NYISO's Comment : Operator Action
126262 BUCHANAN N 345.00 | 1.0549 | 1.0436 | SIN:280 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126360 [BUCHNTA5 138.00] TO BUS 126262 [BUCHANAN N 345.00] CKT 1
126272 E13ST 45 345.00 | 1.0545 | 1.0482 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126273 E13ST 46 345.00 | 1.0546 | 1.0484 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126274 E13ST 47 345.00 | 1.0542 | 1.0476 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126275 E13ST 48 345.00 | 1.0538 | 1.0472 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126277 FARRAGUT 345.00 | 1.0544 | 1.0481 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126280 FARRAGUT TX9345.00 | 1.0562 | 1.0481 | OPEN LINE FROM BUS 126280 [FARRAGUT TX9345.00] TO BUS 126645 [FARRAGUT EAS345.00] CKT 1
126288 IP2 345 345.00 | 1.0555 | 1.0443 | SIN:280 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126360 [BUCHNTA5 138.00] TO BUS 126262 [BUCHANAN N 345.00] CKT 1 | NYISO's Comment : Operator Action
126295 RAINEY 345.00 | 1.0583 | 1.0527 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126304 W 49 ST 345.00 | 1.056 | 1.0498 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126355 BRNVL1&9 138.00 | 0.9062 | 0.9984 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126356 BRNVL2&6 138.00 | 0.9158 | 1.0024 | SB:FARR345_2E TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1 OPEN LINE FROM BUS 126410 [FGT_X3 138.00] TO BUS 126450 [WATER TX2 138.00] CKT 1OPEN LINE FROM BUS 126410 [FGT_X3 138.00] TO BUS 126645 [FARRAGUT EAS345.00] CKT 1OPEN LINE FROM BUS 126450 [WATER TX2 138.00] TO BUS 126619 [WATER ST 27.000] CKT 2TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126404 [FGT_Y3 138.00] CKT 1 OPEN LINE FROM BUS 126404 [FGT_Y3 138.00] TO BUS 126355 [BRNVL1&9 138.00] CKT 1OPEN LINE FROM BUS 126355 [BRNVL1&9 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126355 [BRNVL1&9 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1
126357 BRNVL3&7 138.00 | 0.9097 | 1.0026 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126358 BRNVL4&8 138.00 | 0.9059 | 0.9983 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126378 EASTVIEW 138.00 | 0.9318 | 0.9907 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126380 ELMSFD1E 138.00 | 0.9293 | 0.9889 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126381 ELMSFD1W 138.00 | 0.9292 | 0.9888 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126382 ELMSFD2E 138.00 | 0.9288 | 0.9884 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126383 ELMSFD2W 138.00 | 0.9292 | 0.9887 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126391 E75 ST-2 138.00 | 0.9358 | 1.0004 | SB:RAIN345_8W OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126738 [RNY 7WGT 13.000] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126479 [RAINEY7W 138.00] CKT 1OPEN LINE FROM BUS 126479 [RAINEY7W 138.00] TO BUS 126535 [EAST75 TAP 1138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126393 [E75 ST-4 138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126530 [W110 3&8 138.00] CKT 1OPEN LINE FROM BUS 126393 [E75 ST-4 138.00] TO BUS 126723 [E75TH ST 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126750 [W110ST#1 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126751 [W110ST#2 13.800] CKT 1OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126865 [RAV3 60M 345.00] CKT 2OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126866 [RAV3 60L 345.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126507 [VERNON-W 138.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126562 [8W DUM 138.00] CKT 1REMOVE UNIT 1 FROM BUS 126678 [RNYGT911 13.800]
126392 E75 ST-3 138.00 | 0.9462 | 1.0241 | SB:RAIN345_8W OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126738 [RNY 7WGT 13.000] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126479 [RAINEY7W 138.00] CKT 1OPEN LINE FROM BUS 126479 [RAINEY7W 138.00] TO BUS 126535 [EAST75 TAP 1138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126393 [E75 ST-4 138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126530 [W110 3&8 138.00] CKT 1OPEN LINE FROM BUS 126393 [E75 ST-4 138.00] TO BUS 126723 [E75TH ST 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126750 [W110ST#1 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126751 [W110ST#2 13.800] CKT 1OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126865 [RAV3 60M 345.00] CKT 2OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126866 [RAV3 60L 345.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126507 [VERNON-W 138.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126562 [8W DUM 138.00] CKT 1REMOVE UNIT 1 FROM BUS 126678 [RNYGT911 13.800]
126404 FGT_Y3 138.00 | 0.9217 | 1.0057 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126405 FGT_Y4 138.00 | 0.9317 | 1.0103 | SB:FARR345_2E TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1 OPEN LINE FROM BUS 126410 [FGT_X3 138.00] TO BUS 126450 [WATER TX2 138.00] CKT 1OPEN LINE FROM BUS 126410 [FGT_X3 138.00] TO BUS 126645 [FARRAGUT EAS345.00] CKT 1OPEN LINE FROM BUS 126450 [WATER TX2 138.00] TO BUS 126619 [WATER ST 27.000] CKT 2TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126404 [FGT_Y3 138.00] CKT 1 OPEN LINE FROM BUS 126404 [FGT_Y3 138.00] TO BUS 126355 [BRNVL1&9 138.00] CKT 1OPEN LINE FROM BUS 126355 [BRNVL1&9 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126355 [BRNVL1&9 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1
126406 FGT_Y1 138.00 | 0.9257 | 1.0102 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126407 FGT_Y6 138.00 | 0.9219 | 1.0058 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126408 FGT_X1 138.00 | 0.9456 | 0.9946 | SB:FARR345_3W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126407 [FGT_Y6 138.00] CKT 1 OPEN LINE FROM BUS 126407 [FGT_Y6 138.00] TO BUS 126358 [BRNVL4&8 138.00] CKT 1OPEN LINE FROM BUS 126358 [BRNVL4&8 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126358 [BRNVL4&8 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126413 [FGT_X6 138.00] CKT 1 OPEN LINE FROM BUS 126413 [FGT_X6 138.00] TO BUS 126400 [PLYM_X2 138.00] CKT 1OPEN LINE FROM BUS 126400 [PLYM_X2 138.00] TO BUS 126618 [PLYMOUTH 27.000] CKT 1
126410 FGT_X3 138.00 | 0.7849 | 1.0104 | SB:FARR345_4E TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126272 [E13ST 45 345.00] CKT 1 OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126495 [T14MPT 138.00] CKT 14 OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126871 [E13 TX15 T 138.00] CKT 15 OPEN LINE FROM BUS 126495 [T14MPT 138.00] TO BUS 126496 [T14 13.800] CKT 14 OPEN LINE FROM BUS 126495 [T14MPT 138.00] TO BUS 126872 [E13 TX14 T 138.00] CKT 14 OPEN LINE FROM BUS 126872 [E13 TX14 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126871 [E13 TX15 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126394 [FGT_Y5 138.00] CKT 1 OPEN LINE FROM BUS 126394 [FGT_Y5 138.00] TO BUS 126487 [SEPRT 4&8 138.00] CKT 1OPEN LINE FROM BUS 126487 [SEPRT 4&8 138.00] TO BUS 126740 [SEAPORT NO2 13.800] CKT 1OPEN LINE FROM BUS 126487 [SEPRT 4&8 138.00] TO BUS 126459 [SEAPORT NO1 13.800] CKT 1TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126412 [FGT_X5 138.00] CKT 1 OPEN LINE FROM BUS 126412 [FGT_X5 138.00] TO BUS 126435 [HUDSON 138.00] CKT 1OPEN LINE FROM BUS 126412 [FGT_X5 138.00] TO BUS 126449 [WATER TX1 138.00] CKT 1OPEN LINE FROM BUS 126449 [WATER TX1 138.00] TO BUS 126619 [WATER ST 27.000] CKT 1OPEN LINE FROM BUS 126435 [HUDSON 138.00] TO BUS 126671 [HUDSON 3-4-513.800] CKT 1
126411 FGT_X4 138.00 | 0.7824 | 1.0104 | SB:FARR345_4E TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126272 [E13ST 45 345.00] CKT 1 OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126495 [T14MPT 138.00] CKT 14 OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126871 [E13 TX15 T 138.00] CKT 15 OPEN LINE FROM BUS 126495 [T14MPT 138.00] TO BUS 126496 [T14 13.800] CKT 14 OPEN LINE FROM BUS 126495 [T14MPT 138.00] TO BUS 126872 [E13 TX14 T 138.00] CKT 14 OPEN LINE FROM BUS 126872 [E13 TX14 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126871 [E13 TX15 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126394 [FGT_Y5 138.00] CKT 1 OPEN LINE FROM BUS 126394 [FGT_Y5 138.00] TO BUS 126487 [SEPRT 4&8 138.00] CKT 1OPEN LINE FROM BUS 126487 [SEPRT 4&8 138.00] TO BUS 126740 [SEAPORT NO2 13.800] CKT 1OPEN LINE FROM BUS 126487 [SEPRT 4&8 138.00] TO BUS 126459 [SEAPORT NO1 13.800] CKT 1TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126412 [FGT_X5 138.00] CKT 1 OPEN LINE FROM BUS 126412 [FGT_X5 138.00] TO BUS 126435 [HUDSON 138.00] CKT 1OPEN LINE FROM BUS 126412 [FGT_X5 138.00] TO BUS 126449 [WATER TX1 138.00] CKT 1OPEN LINE FROM BUS 126449 [WATER TX1 138.00] TO BUS 126619 [WATER ST 27.000] CKT 1OPEN LINE FROM BUS 126435 [HUDSON 138.00] TO BUS 126671 [HUDSON 3-4-513.800] CKT 1 | NYISO's Comment : Operator Action
126412 FGT_X5 138.00 | 0.8104 | 1.0115 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126435 HUDSON 138.00 | 0.8104 | 1.0115 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126439 HARR TX1 138.00 | 0.9222 | 0.9827 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126440 HARR TX2 138.00 | 0.9227 | 0.9831 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126441 HARR TX 3 138.00 | 0.9223 | 0.9828 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126499 T11MPT 138.00 | 1.0641 | 1.0575 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126514 WATER TX3 138.00 | 0.7811 | 1.01 | SB:FARR345_4E TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126272 [E13ST 45 345.00] CKT 1 OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126495 [T14MPT 138.00] CKT 14 OPEN LINE FROM BUS 126272 [E13ST 45 345.00] TO BUS 126871 [E13 TX15 T 138.00] CKT 15 OPEN LINE FROM BUS 126495 [T14MPT 138.00] TO BUS 126496 [T14 13.800] CKT 14 OPEN LINE FROM BUS 126495 [T14MPT 138.00] TO BUS 126872 [E13 TX14 T 138.00] CKT 14 OPEN LINE FROM BUS 126872 [E13 TX14 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126871 [E13 TX15 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126394 [FGT_Y5 138.00] CKT 1 OPEN LINE FROM BUS 126394 [FGT_Y5 138.00] TO BUS 126487 [SEPRT 4&8 138.00] CKT 1OPEN LINE FROM BUS 126487 [SEPRT 4&8 138.00] TO BUS 126740 [SEAPORT NO2 13.800] CKT 1OPEN LINE FROM BUS 126487 [SEPRT 4&8 138.00] TO BUS 126459 [SEAPORT NO1 13.800] CKT 1TRIP BRANCH FROM BUS 126645 [FARRAGUT EAS345.00] TO BUS 126412 [FGT_X5 138.00] CKT 1 OPEN LINE FROM BUS 126412 [FGT_X5 138.00] TO BUS 126435 [HUDSON 138.00] CKT 1OPEN LINE FROM BUS 126412 [FGT_X5 138.00] TO BUS 126449 [WATER TX1 138.00] CKT 1OPEN LINE FROM BUS 126449 [WATER TX1 138.00] TO BUS 126619 [WATER ST 27.000] CKT 1OPEN LINE FROM BUS 126435 [HUDSON 138.00] TO BUS 126671 [HUDSON 3-4-513.800] CKT 1
126517 REACM51 345.00 | 1.0611 | 1.0555 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126518 REACM52 345.00 | 1.0611 | 1.0555 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126519 WHITE P TX1 138.00 | 0.9272 | 0.987 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126522 38W02 T 138.00 | 0.9271 | 0.9871 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126523 38W13 T 138.00 | 0.9271 | 0.987 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126524 38W14 T 138.00 | 0.9266 | 0.9866 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126531 W110 2&7 138.00 | 0.9453 | 1.0237 | SB:RAIN345_8W OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126738 [RNY 7WGT 13.000] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126479 [RAINEY7W 138.00] CKT 1OPEN LINE FROM BUS 126479 [RAINEY7W 138.00] TO BUS 126535 [EAST75 TAP 1138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126393 [E75 ST-4 138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126530 [W110 3&8 138.00] CKT 1OPEN LINE FROM BUS 126393 [E75 ST-4 138.00] TO BUS 126723 [E75TH ST 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126750 [W110ST#1 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126751 [W110ST#2 13.800] CKT 1OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126865 [RAV3 60M 345.00] CKT 2OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126866 [RAV3 60L 345.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126507 [VERNON-W 138.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126562 [8W DUM 138.00] CKT 1REMOVE UNIT 1 FROM BUS 126678 [RNYGT911 13.800]
126533 W110 4&10 138.00 | 0.9338 | 0.9997 | SB:RAIN345_8W OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126738 [RNY 7WGT 13.000] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126479 [RAINEY7W 138.00] CKT 1OPEN LINE FROM BUS 126479 [RAINEY7W 138.00] TO BUS 126535 [EAST75 TAP 1138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126393 [E75 ST-4 138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126530 [W110 3&8 138.00] CKT 1OPEN LINE FROM BUS 126393 [E75 ST-4 138.00] TO BUS 126723 [E75TH ST 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126750 [W110ST#1 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126751 [W110ST#2 13.800] CKT 1OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126865 [RAV3 60M 345.00] CKT 2OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126866 [RAV3 60L 345.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126507 [VERNON-W 138.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126562 [8W DUM 138.00] CKT 1REMOVE UNIT 1 FROM BUS 126678 [RNYGT911 13.800]
126534 W110 5&9 138.00 | 0.9452 | 0.9964 | SB:RAIN345_8W OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126738 [RNY 7WGT 13.000] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126479 [RAINEY7W 138.00] CKT 1OPEN LINE FROM BUS 126479 [RAINEY7W 138.00] TO BUS 126535 [EAST75 TAP 1138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126393 [E75 ST-4 138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126530 [W110 3&8 138.00] CKT 1OPEN LINE FROM BUS 126393 [E75 ST-4 138.00] TO BUS 126723 [E75TH ST 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126750 [W110ST#1 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126751 [W110ST#2 13.800] CKT 1OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126865 [RAV3 60M 345.00] CKT 2OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126866 [RAV3 60L 345.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126507 [VERNON-W 138.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126562 [8W DUM 138.00] CKT 1REMOVE UNIT 1 FROM BUS 126678 [RNYGT911 13.800]
126536 EAST75 TAP 4138.00 | 0.9238 | 1.0024 | SB:RAIN345_8W OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126738 [RNY 7WGT 13.000] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126479 [RAINEY7W 138.00] CKT 1OPEN LINE FROM BUS 126479 [RAINEY7W 138.00] TO BUS 126535 [EAST75 TAP 1138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126393 [E75 ST-4 138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126530 [W110 3&8 138.00] CKT 1OPEN LINE FROM BUS 126393 [E75 ST-4 138.00] TO BUS 126723 [E75TH ST 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126750 [W110ST#1 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126751 [W110ST#2 13.800] CKT 1OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126865 [RAV3 60M 345.00] CKT 2OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126866 [RAV3 60L 345.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126507 [VERNON-W 138.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126562 [8W DUM 138.00] CKT 1REMOVE UNIT 1 FROM BUS 126678 [RNYGT911 13.800]
126537 EAST75 TAP 3138.00 | 0.9465 | 1.0243 | SB:RAIN345_8W OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126642 [RAINEY WEST 345.00] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126738 [RNY 7WGT 13.000] CKT 1OPEN LINE FROM BUS 126560 [7WDUM 138.00] TO BUS 126479 [RAINEY7W 138.00] CKT 1OPEN LINE FROM BUS 126479 [RAINEY7W 138.00] TO BUS 126535 [EAST75 TAP 1138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126393 [E75 ST-4 138.00] CKT 1OPEN LINE FROM BUS 126535 [EAST75 TAP 1138.00] TO BUS 126530 [W110 3&8 138.00] CKT 1OPEN LINE FROM BUS 126393 [E75 ST-4 138.00] TO BUS 126723 [E75TH ST 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126750 [W110ST#1 13.800] CKT 1OPEN LINE FROM BUS 126530 [W110 3&8 138.00] TO BUS 126751 [W110ST#2 13.800] CKT 1OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126865 [RAV3 60M 345.00] CKT 2OPEN LINE FROM BUS 126652 [RAV 3 22.000] TO BUS 126866 [RAV3 60L 345.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126507 [VERNON-W 138.00] CKT 1OPEN LINE FROM BUS 126481 [RAINEY8W 138.00] TO BUS 126562 [8W DUM 138.00] CKT 1REMOVE UNIT 1 FROM BUS 126678 [RNYGT911 13.800]
126539 W42 T1&9 138.00 | 0.8791 | 1.0085 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126540 W42 T3&7 138.00 | 0.8946 | 1.0074 | SB:W49_2 TRIP BRANCH FROM BUS 126546 [W49 ST 4 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126542 W42ST5&8 138.00 | 0.8861 | 1.0043 | SB:W49_BTN OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1TRIP BRANCH FROM BUS 126545 [W49 ST 3 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126545 W49 ST 3 138.00 | 0.8862 | 1.0046 | SB:W49_BTN OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1TRIP BRANCH FROM BUS 126545 [W49 ST 3 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Operator Action
126546 W49 ST 4 138.00 | 0.8948 | 1.0079 | SB:W49_2 TRIP BRANCH FROM BUS 126546 [W49 ST 4 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Operator Action
126547 W49 ST 5 138.00 | 0.8793 | 1.0091 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126548 ASTOR T3 TAP138.00 | 0.8793 | 1.0091 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126549 ASTOR T1 TAP138.00 | 0.8948 | 1.0078 | SB:W49_2 TRIP BRANCH FROM BUS 126546 [W49 ST 4 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Operator Action
126550 ASTOR T4 TAP138.00 | 0.8862 | 1.0045 | SB:W49_BTN OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1TRIP BRANCH FROM BUS 126545 [W49 ST 3 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Operator Action
126553 W65ST1&6 138.00 | 0.8793 | 1.0085 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126554 W65ST2&5 138.00 | 0.8948 | 1.0073 | SB:W49_2 TRIP BRANCH FROM BUS 126546 [W49 ST 4 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126555 W65ST3&8 138.00 | 0.8863 | 1.0038 | SB:W49_BTN OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1TRIP BRANCH FROM BUS 126545 [W49 ST 3 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Operator Action
126590 GOWANUS 41SR345.00 | 1.0542 | 1.0481 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126591 GOWANUS 42SR345.00 | 1.0542 | 1.0481 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126592 SEAPT T3&10 138.00 | 0.9197 | 1.0073 | SB:FARR345_8W OPEN LINE FROM BUS 126273 [E13ST 46 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 126273 [E13ST 46 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126273 [E13ST 46 345.00] TO BUS 126497 [T13MPT 138.00] CKT 13 OPEN LINE FROM BUS 126273 [E13ST 46 345.00] TO BUS 126873 [E13 TX12 T 138.00] CKT 12 OPEN LINE FROM BUS 126873 [E13 TX12 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126497 [T13MPT 138.00] TO BUS 126498 [T13 13.800] CKT 13 OPEN LINE FROM BUS 126497 [T13MPT 138.00] TO BUS 126874 [E13 TX13 T 138.00] CKT 13 OPEN LINE FROM BUS 126874 [E13 TX13 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126396 [FGT_Y10 138.00] CKT 1 OPEN LINE FROM BUS 126396 [FGT_Y10 138.00] TO BUS 126504 [38M13 TAP 138.00] CKT 1OPEN LINE FROM BUS 126504 [38M13 TAP 138.00] TO BUS 126592 [SEAPT T3&10 138.00] CKT 1OPEN LINE FROM BUS 126504 [38M13 TAP 138.00] TO BUS 126502 [TRADE TX2 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126436 [FGT_X10 138.00] CKT 1 OPEN LINE FROM BUS 126436 [FGT_X10 138.00] TO BUS 126464 [TAP X10 138.00] CKT 1OPEN LINE FROM BUS 126464 [TAP X10 138.00] TO BUS 126452 [HUDAVE E 138.00] CKT 1
126596 W42 TX7 138.00 | 0.8946 | 1.0073 | SB:W49_2 TRIP BRANCH FROM BUS 126546 [W49 ST 4 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126598 W42 T8 138.00 | 0.8861 | 1.0042 | SB:W49_BTN OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1TRIP BRANCH FROM BUS 126545 [W49 ST 3 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126599 W42 TX9 138.00 | 0.8791 | 1.0084 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 | NYISO's Comment : Operator Action
126600 REAC71 345.00 | 1.0609 | 1.0558 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's Comment : Operator Action
126601 REAC72 345.00 | 1.061 | 1.0559 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126628 MHTX1 138.00 | 0.89 | 1.0094 | SB:MOTT345_2 OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126628 [MHTX1 138.00] CKT 1OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126770 [MH TR8 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR | NYISO's Comment : Operator Action
126629 PARK1 138.00 | 0.8907 | 1.0084 | SB:MOTT345_2 OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126628 [MHTX1 138.00] CKT 1OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126770 [MH TR8 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR | NYISO's Comment : Operator Action
126630 MOTT TX2 138.00 | 0.8899 | 1.0093 | SB:MOTT345_2 OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126628 [MHTX1 138.00] CKT 1OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126336 [MH DUM 8 138.00] TO BUS 126770 [MH TR8 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR | NYISO's Comment : Operator Action
126631 MHTX2 138.00 | 0.8885 | 1.0093 | SB:MOTT345_7 OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126631 [MHTX2 138.00] CKT 1OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126771 [MH TR9 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126632 PARK2 138.00 | 0.8892 | 1.0083 | SB:MOTT345_7 OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126631 [MHTX2 138.00] CKT 1OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126771 [MH TR9 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126633 MOTT TX1 138.00 | 0.8885 | 1.0092 | SB:MOTT345_7 OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126631 [MHTX2 138.00] CKT 1OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126337 [MH DUM 9 138.00] TO BUS 126771 [MH TR9 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126634 MHTX3 138.00 | 0.8886 | 1.0092 | SB:MOTT345_3 OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126634 [MHTX3 138.00] CKT 1OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126772 [MH TR7 T 13.600] CKT 1OPEN LINE FROM BUS 126601 [REAC72 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 4OPEN LINE FROM BUS 126601 [REAC72 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126635 PARK3 138.00 | 0.8893 | 1.0083 | SB:MOTT345_3 OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126634 [MHTX3 138.00] CKT 1OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126772 [MH TR7 T 13.600] CKT 1OPEN LINE FROM BUS 126601 [REAC72 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 4OPEN LINE FROM BUS 126601 [REAC72 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126636 MOTT TX3 138.00 | 0.8886 | 1.0092 | SB:MOTT345_3 OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126634 [MHTX3 138.00] CKT 1OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126338 [MH DUM 7 138.00] TO BUS 126772 [MH TR7 T 13.600] CKT 1OPEN LINE FROM BUS 126601 [REAC72 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 4OPEN LINE FROM BUS 126601 [REAC72 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126637 MHTX4 138.00 | 0.8898 | 1.0094 | SB:MOTT345_BTE OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126637 [MHTX4 138.00] CKT 1OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126773 [MH TR6 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126638 PARK4 138.00 | 0.8905 | 1.0084 | SB:MOTT345_BTE OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126637 [MHTX4 138.00] CKT 1OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126773 [MH TR6 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126639 MOTT TX4 138.00 | 0.8897 | 1.0094 | SB:MOTT345_BTE OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126637 [MHTX4 138.00] CKT 1OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 1OPEN LINE FROM BUS 126339 [MH DUM 6 138.00] TO BUS 126773 [MH TR6 T 13.600] CKT 1OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126641 [MOTT HAVEN 345.00] CKT 3OPEN LINE FROM BUS 126600 [REAC71 345.00] TO BUS 126266 [DUNWOODIE 345.00] CKT SR
126641 MOTT HAVEN 345.00 | 1.0593 | 1.0538 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126642 RAINEY WEST 345.00 | 1.0583 | 1.0527 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126643 RAINEY EAST 345.00 | 1.0583 | 1.0527 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126644 FARRAGUT WES345.00 | 1.0544 | 1.0481 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126645 FARRAGUT EAS345.00 | 1.0544 | 1.0481 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126670 HARR T4 138.00 | 0.9244 | 0.9847 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 | NYISO's Comment : Operator Action
126708 GRASSL1 138.00 | 0.9306 | 0.9896 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126709 GRASSL2 138.00 | 0.9306 | 0.9896 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126718 GRASSL3 138.00 | 0.9306 | 0.9896 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126725 ASTOR T3 138.00 | 0.8793 | 1.0091 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126726 ASTOR T1 138.00 | 0.8948 | 1.0078 | SB:W49_2 TRIP BRANCH FROM BUS 126546 [W49 ST 4 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126727 ASTOR T4 138.00 | 0.8862 | 1.0045 | SB:W49_BTN OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1TRIP BRANCH FROM BUS 126545 [W49 ST 3 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126747 WHITE P TX2 138.00 | 0.9268 | 0.9868 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126748 WHITEP TX2 138.00 | 0.9265 | 0.9865 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126749 WHITEP T7 138.00 | 0.927 | 0.9869 | T:W99&W93 TRIP BRANCH FROM BUS 126262 [BUCHANAN N 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126267 [E VIEW 2N 345.00] CKT 1 TRIP BRANCH FROM BUS 126291 [MILLWOOD 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1 TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 2 TRIP BRANCH FROM BUS 126378 [EASTVIEW 138.00] TO BUS 126269 [E VIEW 2S 345.00] CKT 1
126759 CHERY-T4 138.00 | 0.9485 | 1.0006 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126760 CHERY-T2 138.00 | 0.9481 | 1.0001 | SB:FARR345_2W OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 147829 [ASTOR345 345.00] CKT 1OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126499 [T11MPT 138.00] CKT 11 OPEN LINE FROM BUS 126275 [E13ST 48 345.00] TO BUS 126867 [E13 TX10 T 138.00] CKT 10 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126500 [T11 13.800] CKT 11 OPEN LINE FROM BUS 126499 [T11MPT 138.00] TO BUS 126868 [E13 TX11 T 138.00] CKT 11 OPEN LINE FROM BUS 126868 [E13 TX11 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1OPEN LINE FROM BUS 126867 [E13 TX10 T 138.00] TO BUS 126384 [E13 ST 138.00] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126405 [FGT_Y4 138.00] CKT 1 OPEN LINE FROM BUS 126405 [FGT_Y4 138.00] TO BUS 126356 [BRNVL2&6 138.00] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126604 [BRNSVL#1 27.000] CKT 1OPEN LINE FROM BUS 126356 [BRNVL2&6 138.00] TO BUS 126605 [BRNSVL#2 27.000] CKT 1TRIP BRANCH FROM BUS 126644 [FARRAGUT WES345.00] TO BUS 126411 [FGT_X4 138.00] CKT 1 OPEN LINE FROM BUS 126411 [FGT_X4 138.00] TO BUS 126514 [WATER TX3 138.00] CKT 1OPEN LINE FROM BUS 126514 [WATER TX3 138.00] TO BUS 126619 [WATER ST 27.000] CKT 3
126776 ACADEMY 8DUM138.00 | 1.0994 | 1.0957 | SB:MARC_765_7402 TRIP BRANCH FROM BUS 147828 [MASS 765 765.00] TO BUS 180819 [CHA-NY 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147828 [MASS 765 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 2
126777 ACADEMY 1DUM138.00 | 1.1005 | 1.0968 | SB:MARC_765_7402 TRIP BRANCH FROM BUS 147828 [MASS 765 765.00] TO BUS 180819 [CHA-NY 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147828 [MASS 765 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 2
126780 SCK-PARW 138.00 | 1.0922 | 1.0886 | SB:MARC_765_7402 TRIP BRANCH FROM BUS 147828 [MASS 765 765.00] TO BUS 180819 [CHA-NY 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147828 [MASS 765 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 2
126781 SCK-PARE 138.00 | 1.0922 | 1.0886 | SB:MARC_765_7402 TRIP BRANCH FROM BUS 147828 [MASS 765 765.00] TO BUS 180819 [CHA-NY 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147828 [MASS 765 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 2
126828 W50-TAP TX 5138.00 | 0.8948 | 1.0078 | SB:W49_2 TRIP BRANCH FROM BUS 126546 [W49 ST 4 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1 OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT SR OPEN LINE FROM BUS 126517 [REACM51 345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126847 ACADEMY 345.00 | 0.8327 | 1.0292 | SB:SPRA345_RNS2 OPEN LINE FROM BUS 126299 [REACBUS 345.00] TO BUS 147857 [DVNPT NK 345.00] CKT 1OPEN LINE FROM BUS 126299 [REACBUS 345.00] TO BUS 126298 [SPRAINBROOK 345.00] CKT BY OPEN LINE FROM BUS 147857 [DVNPT NK 345.00] TO BUS 128830 [HMP HRBR 345.00] CKT 1OPEN LINE FROM BUS 128830 [HMP HRBR 345.00] TO BUS 128824 [EGC DUM 345.00] CKT 1OPEN LINE FROM BUS 128824 [EGC DUM 345.00] TO BUS 128825 [EGC PAR 345.00] CKT 1OPEN LINE FROM BUS 128825 [EGC PAR 345.00] TO BUS 128822 [E.G.C.-1 345.00] CKT 1OPEN LINE FROM BUS 128825 [EGC PAR 345.00] TO BUS 128823 [E.G.C.-2 345.00] CKT 1TRIP BRANCH FROM BUS 126298 [SPRAINBROOK 345.00] TO BUS 126847 [ACADEMY 345.00] CKT 1 | NYISO's Comment : Local RR Exception
126865 RAV3 60M 345.00 | 1.0752 | 1.0528 | OPEN LINE FROM BUS 126643 [RAINEY EAST 345.00] TO BUS 126865 [RAV3 60M 345.00] CKT 1
126866 RAV3 60L 345.00 | 1.0752 | 1.0528 | OPEN LINE FROM BUS 126642 [RAINEY WEST 345.00] TO BUS 126866 [RAV3 60L 345.00] CKT 1
128248 ANNTRHIGH 345.00 | 1.0535 | 1.0455 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's Comment : Operator Action
128701 ASTOR REAC 345.00 | 1.0535 | 1.0455 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
130756 STOLE345 345.00 | 1.0612 | 0.9992 | S:STOLLE345 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 1 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 2
130757 WATRC345 345.00 | 1.052 | 1.0421 | SB:WATRC345_31-2 TRIP BRANCH FROM BUS 130755 [OAKDL345 345.00] TO BUS 130757 [WATRC345 345.00] CKT 1 TRIP BRANCH FROM BUS 130757 [WATRC345 345.00] TO BUS 130768 [WATRC230 230.00] CKT 2
130790 COOPC115 115.00 | 1.0529 | 1.0359 | T:34&42A_CE18/UC30 TRIP BRANCH FROM BUS 148995 [CPV_VALY 345.00] TO BUS 130750 [COOPC345 345.00] CKT 2 OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 146772 [SHOEMTAP 138.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 125001 [ROCK TAV 345.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 130750 [COOPC345 345.00] CKT 1
130842 PAWLN115 115.00 | 0.9329 | 0.9737 | SB:FISH345_6 OPEN LINE FROM BUS 126305 [WOOD A 345.00] TO BUS 130758 [WOODA345 345.00] CKT 1OPEN LINE FROM BUS 126305 [WOOD A 345.00] TO BUS 126281 [E FISHKILL 345.00] CKT 1OPEN LINE FROM BUS 126305 [WOOD A 345.00] TO BUS 126293 [PL VILLW 345.00] CKT 1OPEN LINE FROM BUS 130758 [WOODA345 345.00] TO BUS 130865 [WOODS115 115.00] CKT 1TRIP BRANCH FROM BUS 126281 [E FISHKILL 345.00] TO BUS 125022 [E FISH I 115.00] CKT 1
131553 MTNDL115 115.00 | 1.0542 | 1.0386 | T:34&42A_CE18/UC30 TRIP BRANCH FROM BUS 148995 [CPV_VALY 345.00] TO BUS 130750 [COOPC345 345.00] CKT 2 OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 146772 [SHOEMTAP 138.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 125001 [ROCK TAV 345.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 130750 [COOPC345 345.00] CKT 1
131554 ROCKH115 115.00 | 1.053 | 1.0369 | T:34&42A_CE18/UC30 TRIP BRANCH FROM BUS 148995 [CPV_VALY 345.00] TO BUS 130750 [COOPC345 345.00] CKT 2 OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 146772 [SHOEMTAP 138.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 125001 [ROCK TAV 345.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 130750 [COOPC345 345.00] CKT 1
135303 SAWYER77 230.00 | 0.9346 | 1.0231 | SB:HUNT230_R1302 TRIP BRANCH FROM BUS 135415 [PACKARD2 230.00] TO BUS 135303 [SAWYER77 230.00] CKT 1 TRIP BRANCH FROM BUS 135303 [SAWYER77 230.00] TO BUS 135414 [HUNTLEY2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135305 [SAWYER80 230.00] CKT 1 OPEN LINE FROM BUS 135800 [HNTLY67G 13.800] TO BUS 135414 [HUNTLEY2 230.00] CKT 1
135304 SAWYER78 230.00 | 0.9379 | 1.0229 | SB:HUNT230_R1501 TRIP BRANCH FROM BUS 135304 [SAWYER78 230.00] TO BUS 135415 [PACKARD2 230.00] CKT 2 TRIP BRANCH FROM BUS 135304 [SAWYER78 230.00] TO BUS 135414 [HUNTLEY2 230.00] CKT 2 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135306 [SAWYER79 230.00] CKT 1 OPEN LINE FROM BUS 135801 [HNTLY68G 13.800] TO BUS 135414 [HUNTLEY2 230.00] CKT 1
135305 SAWYER80 230.00 | 0.9385 | 1.0233 | SB:HUNT230_R1202 TRIP BRANCH FROM BUS 135303 [SAWYER77 230.00] TO BUS 135414 [HUNTLEY2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135305 [SAWYER80 230.00] CKT 1 TRIP BRANCH FROM BUS 135305 [SAWYER80 230.00] TO BUS 135419 [SUNY-80 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135419 [SUNY-80 230.00] CKT 1 OPEN LINE FROM BUS 135800 [HNTLY67G 13.800] TO BUS 135414 [HUNTLEY2 230.00] CKT 1
135307 SAWYERB1 230.00 | 0.9346 | 1.0231 | SB:HUNT230_R1302 TRIP BRANCH FROM BUS 135415 [PACKARD2 230.00] TO BUS 135303 [SAWYER77 230.00] CKT 1 TRIP BRANCH FROM BUS 135303 [SAWYER77 230.00] TO BUS 135414 [HUNTLEY2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135305 [SAWYER80 230.00] CKT 1 OPEN LINE FROM BUS 135800 [HNTLY67G 13.800] TO BUS 135414 [HUNTLEY2 230.00] CKT 1
135308 SAWYERB2 230.00 | 0.9379 | 1.0229 | SB:HUNT230_R1501 TRIP BRANCH FROM BUS 135304 [SAWYER78 230.00] TO BUS 135415 [PACKARD2 230.00] CKT 2 TRIP BRANCH FROM BUS 135304 [SAWYER78 230.00] TO BUS 135414 [HUNTLEY2 230.00] CKT 2 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135306 [SAWYER79 230.00] CKT 1 OPEN LINE FROM BUS 135801 [HNTLY68G 13.800] TO BUS 135414 [HUNTLEY2 230.00] CKT 1
135309 SAWYERB3 230.00 | 0.9385 | 1.0233 | SB:HUNT230_R1202 TRIP BRANCH FROM BUS 135303 [SAWYER77 230.00] TO BUS 135414 [HUNTLEY2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135305 [SAWYER80 230.00] CKT 1 TRIP BRANCH FROM BUS 135305 [SAWYER80 230.00] TO BUS 135419 [SUNY-80 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135419 [SUNY-80 230.00] CKT 1 OPEN LINE FROM BUS 135800 [HNTLY67G 13.800] TO BUS 135414 [HUNTLEY2 230.00] CKT 1
135398 SW345 345.00 | 1.0549 | 1.0249 | S:STOLLE345 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 1 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 2
135411 ELM-71 230.00 | 0.9102 | 1.0253 | OPEN LINE FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135416 [SENCA-71 230.00] CKT 1
135412 ELM-72 230.00 | 0.9061 | 1.0253 | SB:GARD230_R823 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135450 [GRDNVL1 115.00] CKT 3 TRIP BRANCH FROM BUS 135418 [SUNY-79 230.00] TO BUS 135413 [GRDNVL2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135306 [SAWYER79 230.00] CKT 1 TRIP BRANCH FROM BUS 135306 [SAWYER79 230.00] TO BUS 135418 [SUNY-79 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135417 [SENCA-72 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 130762 [GARDV230 230.00] CKT 1
135416 SENCA-71 230.00 | 0.9098 | 1.0255 | OPEN LINE FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135416 [SENCA-71 230.00] CKT 1
135417 SENCA-72 230.00 | 0.9057 | 1.0256 | SB:GARD230_R823 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135450 [GRDNVL1 115.00] CKT 3 TRIP BRANCH FROM BUS 135418 [SUNY-79 230.00] TO BUS 135413 [GRDNVL2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135306 [SAWYER79 230.00] CKT 1 TRIP BRANCH FROM BUS 135306 [SAWYER79 230.00] TO BUS 135418 [SUNY-79 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135417 [SENCA-72 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 130762 [GARDV230 230.00] CKT 1
137201 FRAEDCSC 345.00 | 1.0592 | 1.037 | OPEN LINE FROM BUS 130753 [FRASR345 345.00] TO BUS 130752 [FRASVC18 18.200] CKT 1
137222 CAMDNWIR 115.00 | 0.9475 | 0.9691 | SB:EDIC345_R70 TRIP BRANCH FROM BUS 147833 [MARCY T1 345.00] TO BUS 137200 [EDIC 345.00] CKT 1 TRIP BRANCH FROM BUS 137200 [EDIC 345.00] TO BUS 137210 [PORTER 2 230.00] CKT 1 TRIP BRANCH FROM BUS 137200 [EDIC 345.00] TO BUS 137235 [PORTER 1 115.00] CKT 1
137224 DEERFD-H 115.00 | 1.0549 | 1.0465 | SB:PORT230_R825 TRIP BRANCH FROM BUS 137730 [ROTRDM.2 230.00] TO BUS 137210 [PORTER 2 230.00] CKT 2 TRIP BRANCH FROM BUS 137210 [PORTER 2 230.00] TO BUS 137235 [PORTER 1 115.00] CKT 1
137225 DEERFD-I 115.00 | 1.055 | 1.0466 | SB:PORT230_R825 TRIP BRANCH FROM BUS 137730 [ROTRDM.2 230.00] TO BUS 137210 [PORTER 2 230.00] CKT 2 TRIP BRANCH FROM BUS 137210 [PORTER 2 230.00] TO BUS 137235 [PORTER 1 115.00] CKT 1
137230 LEHIGH 115.00 | 0.9478 | 0.9691 | SB:EDIC345_R140 TRIP BRANCH FROM BUS 137452 [N.SCOT77 345.00] TO BUS 137200 [EDIC 345.00] CKT 1 TRIP BRANCH FROM BUS 137200 [EDIC 345.00] TO BUS 137210 [PORTER 2 230.00] CKT 1 TRIP BRANCH FROM BUS 137200 [EDIC 345.00] TO BUS 137235 [PORTER 1 115.00] CKT 1
137235 PORTER 1 115.00 | 1.0554 | 1.047 | SB:PORT230_R825 TRIP BRANCH FROM BUS 137730 [ROTRDM.2 230.00] TO BUS 137210 [PORTER 2 230.00] CKT 2 TRIP BRANCH FROM BUS 137210 [PORTER 2 230.00] TO BUS 137235 [PORTER 1 115.00] CKT 1
137455 ATHENS 345.00 | 1.0686 | 1.0356 | SB:LEEDS345_R395 TRIP BRANCH FROM BUS 137451 [LEEDS 3 345.00] TO BUS 137455 [ATHENS 345.00] CKT 1 TRIP BRANCH FROM BUS 137451 [LEEDS 3 345.00] TO BUS 147831 [GILB 345 345.00] CKT 1
137562 EASTOVER RD 230.00 | 0.9445 | 0.9638 | S:EMPIRE OPEN LINE FROM BUS 137454 [REYNLD3 345.00] TO BUS 137558 [GBSH345 345.00] CKT 1OPEN LINE FROM BUS 137454 [REYNLD3 345.00] TO BUS 137528 [REY. RD. 115.00] CKT 1OPEN LINE FROM BUS 137454 [REYNLD3 345.00] TO BUS 137450 [ALPS345 345.00] CKT 1OPEN LINE FROM BUS 137559 [BESI20G1 18.000] TO BUS 137558 [GBSH345 345.00] CKT 1OPEN LINE FROM BUS 137560 [BESI20G2 18.000] TO BUS 137558 [GBSH345 345.00] CKT 1OPEN LINE FROM BUS 137561 [BESI20G3 18.000] TO BUS 137558 [GBSH345 345.00] CKT 1
137927 RECTOR 230.00 | 1.0587 | 1.0404 | T:MAP13&12 TRIP BRANCH FROM BUS 147835 [ADRON B1 230.00] TO BUS 137928 [CHASES L 230.00] CKT 1 TRIP BRANCH FROM BUS 137210 [PORTER 2 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1
137928 CHASES L 230.00 | 1.0565 | 1.0382 | T:MAP13&12 TRIP BRANCH FROM BUS 147835 [ADRON B1 230.00] TO BUS 137928 [CHASES L 230.00] CKT 1 TRIP BRANCH FROM BUS 137210 [PORTER 2 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1
147829 ASTOR345 345.00 | 1.0535 | 1.0455 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
147860 TR-TAP1 115.00 | 0.1762 | 1.0319 | SB:MOSE115_1414 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147849 [MOS 115 115.00] CKT 2 TRIP BRANCH FROM BUS 147849 [MOS 115 115.00] TO BUS 147860 [TR-TAP1 115.00] CKT 1
147864 REYN T#1 115.00 | 0.1764 | 1.0317 | SB:MOSE115_1414 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147849 [MOS 115 115.00] CKT 2 TRIP BRANCH FROM BUS 147849 [MOS 115 115.00] TO BUS 147860 [TR-TAP1 115.00] CKT 1
148010 GM T#1 115.00 | 0.1767 | 1.0312 | SB:MOSE115_1414 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147849 [MOS 115 115.00] CKT 2 TRIP BRANCH FROM BUS 147849 [MOS 115 115.00] TO BUS 147860 [TR-TAP1 115.00] CKT 1
148021 MASS-C 115.00 | 0.1762 | 1.0319 | SB:MOSE115_1414 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147849 [MOS 115 115.00] CKT 2 TRIP BRANCH FROM BUS 147849 [MOS 115 115.00] TO BUS 147860 [TR-TAP1 115.00] CKT 1
148059 MARCCSC1 345.00 | 1.0604 | 1.0473 | T:34&42A_CE18/UC30 TRIP BRANCH FROM BUS 148995 [CPV_VALY 345.00] TO BUS 130750 [COOPC345 345.00] CKT 2 OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 146772 [SHOEMTAP 138.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 125001 [ROCK TAV 345.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 130750 [COOPC345 345.00] CKT 1
148707 Q308_AST2 345.00 | 1.0535 | 1.0452 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
180305 MAN315 315.00 | 0.9419 | 0.9498 | OPEN LINE FROM BUS 180703 [LEV735 735.00] TO BUS 180705 [MAN735 735.00] CKT &3
180309 ARN315 315.00 | 0.9477 | 0.9888 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
180320 RAD315 315.00 | 1.0551 | 1.0343 | SANDY_DC&OMS TRIP BRANCH FROM BUS 107400 [SANDBAR 115.00] TO BUS 107410 [SANDBAR REAC115.00] CKT 2 OPEN LINE FROM BUS 114071 [SNDYPD HVDC1345.00] TO BUS 113950 [SANDY POND 345.00] CKT 1OPEN LINE FROM BUS 114072 [SNDYPD HVDC2345.00] TO BUS 113950 [SANDY POND 345.00] CKT 1
180326 OUT315 315.00 | 1.0925 | 1.0274 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
180405 MAN315 A315.00 | 0.9396 | 0.9498 | OPEN LINE FROM BUS 180305 [MAN315 315.00] TO BUS 180705 [MAN735 735.00] CKT N2
180433 B1-315 315.00 | 0.9109 | 0.9682 | OPEN LINE FROM BUS 180349 [LG2315 315.00] TO BUS 180249 [LG2ABT 13.800] CKT 1
180434 B2-315 315.00 | 0.9234 | 0.9682 | OPEN LINE FROM BUS 180349 [LG2315 315.00] TO BUS 180249 [LG2ABT 13.800] CKT 1
180457 LNF315 315.00 | 1.0534 | 1.0377 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
180458 VGN315 315.00 | 1.0848 | 1.0242 | OPEN LINE FROM BUS 154072 [IPB_MAS_JA41220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
180460 BASQUE 315.00 | 0.9443 | 0.9978 | OPEN LINE FROM BUS 180349 [LG2315 315.00] TO BUS 180249 [LG2ABT 13.800] CKT 1
180462 LAN315 315.00 | 1.0851 | 1.0626 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
180472 RDL315 315.00 | 1.0564 | 1.0396 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180475 LGL315 315.00 | 0.9234 | 0.9765 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180475 [LGL315 315.00] CKT 1
180476 LGL315 A315.00 | 0.9233 | 0.9764 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
180488 MAURIC 315.00 | 1.0847 | 1.0629 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
180490 KAM<A> 315.00 | 1.0772 | 1.0539 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180491 KAM<B> 315.00 | 1.0772 | 1.0539 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180492 KAM<C> 315.00 | 1.0948 | 1.0683 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180493 KAM<D> 315.00 | 1.0948 | 1.0683 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180496 KAM<G> 315.00 | 1.0569 | 1.0328 | OPEN LINE FROM BUS 180492 [KAM<C> 315.00] TO BUS 180496 [KAM<G> 315.00] CKT 1
180497 KAM<H> 315.00 | 1.0569 | 1.0328 | OPEN LINE FROM BUS 180493 [KAM<D> 315.00] TO BUS 180497 [KAM<H> 315.00] CKT 1
180500 MANIC2 315.00 | 0.9423 | 0.952 | OPEN LINE FROM BUS 180305 [MAN315 315.00] TO BUS 180705 [MAN735 735.00] CKT N4
180502 MANIC2 B315.00 | 0.9412 | 0.9512 | OPEN LINE FROM BUS 180305 [MAN315 315.00] TO BUS 180705 [MAN735 735.00] CKT N4
180526 OUTHAW 220.00 | 1.1062 | 1.0905 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
180530 FIG315 315.00 | 0.9326 | 0.96 | OPEN LINE FROM BUS 180530 [FIG315 315.00] TO BUS 181331 [FIG-1 315.00] CKT 1
180535 O2-315 315.00 | 0.948 | 0.9557 | OPEN LINE FROM BUS 180305 [MAN315 315.00] TO BUS 180705 [MAN735 735.00] CKT N2
180536 O3A315 315.00 | 0.9394 | 0.9496 | OPEN LINE FROM BUS 180305 [MAN315 315.00] TO BUS 180705 [MAN735 735.00] CKT N4
180575 MADAWA 315.00 | 1.0984 | 1.054 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180576 DPNA1 315.00 | 1.0747 | 1.0216 | OPEN LINE FROM BUS 154073 [IPB_MAS_JA42220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
180577 PNA1 315.00 | 1.0747 | 1.0216 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
180626 CDP345 345.00 | 1.0651 | 1.063 | OPEN LINE FROM BUS 180632 [DEL345 345.00] TO BUS 180633 [DEL161 161.00] CKT 2
180642 DHR315 315.00 | 0.9493 | 0.9511 | OPEN LINE FROM BUS 180705 [MAN735 735.00] TO BUS 180709 [ARN735 735.00] CKT &2
180643 HTV315 315.00 | 0.9492 | 0.9511 | OPEN LINE FROM BUS 180705 [MAN735 735.00] TO BUS 180709 [ARN735 735.00] CKT &2
180675 MADAWA A345.00 | 1.1226 | 1.0354 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
180676 DPNA2 315.00 | 1.0746 | 1.0215 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
180677 PNA2 315.00 | 1.0746 | 1.0215 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
181020 RAD315 A315.00 | 1.0551 | 1.0343 | SANDY_DC OPEN LINE FROM BUS 114071 [SNDYPD HVDC1345.00] TO BUS 113950 [SANDY POND 345.00] CKT 1OPEN LINE FROM BUS 114072 [SNDYPD HVDC2345.00] TO BUS 113950 [SANDY POND 345.00] CKT 1
181119 CHANY1 120.00 | 1.0679 | 1.0317 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180419 [CHATG 315.00] CKT 1
181128 LBL120 120.00 | 1.0629 | 1.0572 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
181219 CHANY2 120.00 | 1.0679 | 1.0317 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180519 [CHATG2 315.00] CKT 1
181258 VGN120 120.00 | 1.0555 | 1.008 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
181262 LAN120 120.00 | 1.0589 | 1.0365 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
181275 LGL120 120.00 | 0.9462 | 0.9744 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180475 [LGL315 315.00] CKT 1
181283 DELERY 120.00 | 0.9446 | 0.9573 | OPEN LINE FROM BUS 180715 [CHE735 735.00] TO BUS 180719 [CHA735 735.00] CKT 1
181330 FIG120 120.00 | 1.0565 | 1.0563 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 2
181390 THE120 120.00 | 1.0588 | 1.053 | OPEN LINE FROM BUS 180703 [LEV735 735.00] TO BUS 180705 [MAN735 735.00] CKT &3
181419 CHATG4 120.00 | 1.0726 | 1.025 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180519 [CHATG2 315.00] CKT 1
181454 R15EXP 120.00 | 1.0643 | 1.0643 | OPEN LINE FROM BUS 180431 [SAR315 315.00] TO BUS 181231 [SAR120 120.00] CKT 5
181482 CHD120 120.00 | 1.097 | 1.0557 | OPEN LINE FROM BUS 180703 [LEV735 735.00] TO BUS 180705 [MAN735 735.00] CKT &2
181501 BH120A 120.00 | 1.0724 | 1.0453 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180519 [CHATG2 315.00] CKT 1
181503 BH120D 120.00 | 1.0719 | 1.0479 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180419 [CHATG 315.00] CKT 1
181506 CED120 120.00 | 0.9498 | 0.9764 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180475 [LGL315 315.00] CKT 1
181507 CA120A 120.00 | 1.0504 | 1.0457 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
181540 FARMD1 120.00 | 1.0501 | 1.008 | OPEN LINE FROM BUS 154073 [IPB_MAS_JA42220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
181552 RA2120 120.00 | 1.0521 | 1.0519 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
181553 RA7120 120.00 | 1.053 | 1.0529 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
181554 R15120 120.00 | 1.0643 | 1.0643 | SB:GILB345_3208 TRIP BRANCH FROM BUS 137451 [LEEDS 3 345.00] TO BUS 147831 [GILB 345 345.00] CKT 1 OPEN LINE FROM BUS 147777 [GILBOA#1 17.000] TO BUS 147831 [GILB 345 345.00] CKT 1OPEN LINE FROM BUS 147778 [GILBOA#2 17.000] TO BUS 147831 [GILB 345 345.00] CKT 2
181556 PRC120 120.00 | 1.0674 | 1.067 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 2
181615 PERBKA A161.00 | 0.9079 | 0.9233 | OPEN LINE FROM BUS 180718 [SAG735 735.00] TO BUS 181618 [SAG161 161.00] CKT 2
181620 ROMAINE_1 161.00 | 0.9404 | 0.9859 | OPEN LINE FROM BUS 180411 [ROM1-315B 315.00] TO BUS 181620 [ROMAINE_1 161.00] CKT 1
181621 D-ROMAINE 161.00 | 0.9394 | 0.9846 | OPEN LINE FROM BUS 180411 [ROM1-315B 315.00] TO BUS 180421 [ROM1-315A 315.00] CKT 1
181629 HAR155 161.00 | 0.9292 | 0.9602 | OPEN LINE FROM BUS 180710 [MTG735 735.00] TO BUS 180760 [CHU735 735.00] CKT &3
182030 CAR230 230.00 | 0.9304 | 0.9556 | OPEN LINE FROM BUS 180730 [CAR735 735.00] TO BUS 182030 [CAR230 230.00] CKT 2
182056 CANTON A230.00 | 0.9465 | 0.9949 | OPEN LINE FROM BUS 182055 [CAN230 230.00] TO BUS 182056 [CANTON A230.00] CKT 1
182071 RCOEUR A230.00 | 1.0534 | 1.0515 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
182081 CHALLAR A230.00 | 1.0559 | 1.0532 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
182086 SHR230 230.00 | 0.9368 | 0.9748 | OPEN LINE FROM BUS 182055 [CAN230 230.00] TO BUS 182086 [SHR230 230.00] CKT 1
182143 PAU230 230.00 | 1.0964 | 1.0828 | OPEN LINE FROM BUS 154072 [IPB_MAS_JA41220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
182201 GOE230 230.00 | 1.0538 | 1.0423 | OPEN LINE FROM BUS 182201 [GOE230 230.00] TO BUS 181601 [GOE161 161.00] CKT 12
182219 RBLANC 230.00 | 1.0512 | 1.0468 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
182220 TRE230 230.00 | 1.0515 | 1.0494 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
182221 BMT230 230.00 | 1.0521 | 1.0486 | OPEN LINE FROM BUS 182268 [TRV230 230.00] TO BUS 183525 [D_KAPI_230_1230.00] CKT 1
182222 LAT230 230.00 | 1.0534 | 1.0431 | OPEN LINE FROM BUS 182222 [LAT230 230.00] TO BUS 182835 [TUQ230 230.00] CKT 1
182263 CESAIR 230.00 | 0.933 | 0.938 | OPEN LINE FROM BUS 180701 [BCV735 735.00] TO BUS 182001 [BCV230 230.00] CKT 5
182266 SOR230 230.00 | 0.922 | 0.9471 | OPEN LINE FROM BUS 180730 [CAR735 735.00] TO BUS 182030 [CAR230 230.00] CKT 2
182298 QUY230 230.00 | 1.0503 | 1.0495 | OPEN LINE FROM BUS 182143 [PAU230 230.00] TO BUS 181243 [PAU120 120.00] CKT 11
182348 CDC230 230.00 | 1.0672 | 1.0491 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
182749 DQUEVI 120.00 | 1.0627 | 1.057 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
183025 CHENAU 230.00 | 0.8766 | 0.9816 | OPEN LINE FROM BUS 182273 [DCH-D1 230.00] TO BUS 183025 [CHENAU 230.00] CKT 1
183026 CHENAU A230.00 | 0.946 | 0.9819 | OPEN LINE FROM BUS 182274 [DCH-D2 230.00] TO BUS 183026 [CHENAU A230.00] CKT 1
183154 SHELD 161.00 | 0.9255 | 0.9759 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180422 [ROM2-315 315.00] CKT 1
183195 NOR161 161.00 | 0.9154 | 0.9459 | OPEN LINE FROM BUS 180710 [MTG735 735.00] TO BUS 180760 [CHU735 735.00] CKT &3
183384 D-ALOUE3 161.00 | 0.9341 | 0.9613 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183385 ALOUET 161.00 | 0.9341 | 0.9613 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183387 ALOUE2 161.00 | 0.9341 | 0.9613 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183424 DRTONE 161.00 | 0.9237 | 0.9748 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180422 [ROM2-315 315.00] CKT 1
183425 RTONER 161.00 | 0.9237 | 0.9748 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180422 [ROM2-315 315.00] CKT 1
183426 SECT65-19 161.00 | 0.9237 | 0.9748 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180422 [ROM2-315 315.00] CKT 1
183435 HAVRE 161.00 | 0.9233 | 0.9679 | OPEN LINE FROM BUS 180421 [ROM1-315A 315.00] TO BUS 180422 [ROM2-315 315.00] CKT 1
183474 DER_MAGPIE 161.00 | 0.9205 | 0.9729 | OPEN LINE FROM BUS 180421 [ROM1-315A 315.00] TO BUS 180422 [ROM2-315 315.00] CKT 1
183525 D_KAPI_230_1230.00 | 1.0524 | 1.0016 | OPEN LINE FROM BUS 182268 [TRV230 230.00] TO BUS 183525 [D_KAPI_230_1230.00] CKT 1
183616 BOPOR2 315.00 | 0.8915 | 1.0277 | OPEN LINE FROM BUS 183612 [TPBPO2 315.00] TO BUS 183616 [BOPOR2 315.00] CKT 1
183625 AGBOIS 315.00 | 1.0861 | 1.0416 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
183831 AMBTP2 161.00 | 0.9467 | 0.966 | OPEN LINE FROM BUS 180706 [MIC735 735.00] TO BUS 180718 [SAG735 735.00] CKT &1
183832 AMBROD 161.00 | 0.9466 | 0.9659 | OPEN LINE FROM BUS 180706 [MIC735 735.00] TO BUS 180718 [SAG735 735.00] CKT &1
183840 CHINOR 161.00 | 0.9409 | 0.9604 | OPEN LINE FROM BUS 180706 [MIC735 735.00] TO BUS 180718 [SAG735 735.00] CKT &1
183876 DUBCD1 161.00 | 0.9494 | 0.9686 | OPEN LINE FROM BUS 180706 [MIC735 735.00] TO BUS 180718 [SAG735 735.00] CKT &1
183898 DNIOBEC 161.00 | 0.9349 | 0.9545 | OPEN LINE FROM BUS 180706 [MIC735 735.00] TO BUS 180718 [SAG735 735.00] CKT &1
183900 SIMARD 161.00 | 0.9438 | 0.9632 | OPEN LINE FROM BUS 180706 [MIC735 735.00] TO BUS 180718 [SAG735 735.00] CKT &1
183925 DUPOR1 161.00 | 0.9499 | 0.9627 | OPEN LINE FROM BUS 180706 [MIC735 735.00] TO BUS 180718 [SAG735 735.00] CKT &1
184026 DALMA 230.00 | 1.0522 | 1.0147 | OPEN LINE FROM BUS 182132 [IM230 230.00] TO BUS 184026 [DALMA 230.00] CKT 1
184111 GBAIE2 161.00 | 0.9149 | 0.9225 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
184112 GBAIE1 161.00 | 0.9149 | 0.9225 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
184165 MANIWA 120.00 | 1.0839 | 1.0638 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
184245 BOWATR 120.00 | 1.053 | 1.0055 | OPEN LINE FROM BUS 154072 [IPB_MAS_JA41220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
184260 LDILES 120.00 | 1.1139 | 1.0939 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
184264 LIMBD2 120.00 | 1.0501 | 1.008 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
184268 LACROIX-D1 120.00 | 1.0654 | 1.0452 | OPEN LINE FROM BUS 154073 [IPB_MAS_JA42220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
184269 LACROIX-D2 120.00 | 1.0654 | 1.0452 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
184270 LACROIXV-120120.00 | 1.0655 | 1.0454 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
184271 KAZ120-D1 120.00 | 1.0546 | 1.0342 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
184272 KAZ120-D2 120.00 | 1.0546 | 1.0342 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154072 [IPB_MAS_JA41220.00] CKT 1
184275 MLRIER120A 120.00 | 1.1145 | 1.0945 | OPEN LINE FROM BUS 154073 [IPB_MAS_JA42220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
184280 NDLAUS 120.00 | 1.1151 | 1.095 | OPEN LINE FROM BUS 154073 [IPB_MAS_JA42220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
184500 VALLEY 120.00 | 0.9338 | 0.962 | OPEN LINE FROM BUS 180476 [LGL315 A315.00] TO BUS 181275 [LGL120 120.00] CKT 3
184505 MGREMA 120.00 | 0.9368 | 0.9649 | OPEN LINE FROM BUS 180475 [LGL315 315.00] TO BUS 181275 [LGL120 120.00] CKT 2
184508 V-SOULB1 120.00 | 0.9424 | 0.9699 | OPEN LINE FROM BUS 180476 [LGL315 A315.00] TO BUS 181275 [LGL120 120.00] CKT 3
184514 EKADER 120.00 | 0.9329 | 0.9612 | OPEN LINE FROM BUS 180476 [LGL315 A315.00] TO BUS 181275 [LGL120 120.00] CKT 3
184515 LAROCQ 120.00 | 0.933 | 0.9612 | OPEN LINE FROM BUS 180476 [LGL315 A315.00] TO BUS 181275 [LGL120 120.00] CKT 3
184521 RIVSUD315-1 315.00 | 1.1236 | 0.9926 | OPEN LINE FROM BUS 184519 [RIVSUD-D1 315.00] TO BUS 184521 [RIVSUD315-1 315.00] CKT 1
184522 RIVSUD315-2 315.00 | 1.1236 | 0.9926 | OPEN LINE FROM BUS 184520 [RIVSUD-D2 315.00] TO BUS 184522 [RIVSUD315-2 315.00] CKT 1
184579 D-ERIC1 120.00 | 0.9421 | 0.9702 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184580 D-ERIC2 120.00 | 0.9427 | 0.9706 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184584 +REMI_B4 120.00 | 0.9382 | 0.9512 | OPEN LINE FROM BUS 180715 [CHE735 735.00] TO BUS 180719 [CHA735 735.00] CKT 1
184588 SREMD2 120.00 | 0.9403 | 0.9532 | OPEN LINE FROM BUS 180715 [CHE735 735.00] TO BUS 180719 [CHA735 735.00] CKT 1
184650 BRO315 315.00 | 0.9356 | 0.9912 | OPEN LINE FROM BUS 184650 [BRO315 315.00] TO BUS 184651 [BROSD1 315.00] CKT 1
184651 BROSD1 315.00 | 0.9373 | 0.9915 | OPEN LINE FROM BUS 184519 [RIVSUD-D1 315.00] TO BUS 184651 [BROSD1 315.00] CKT 1
184652 BROSD2 315.00 | 0.9368 | 0.9915 | OPEN LINE FROM BUS 184520 [RIVSUD-D2 315.00] TO BUS 184652 [BROSD2 315.00] CKT 1
184653 BRO315 A315.00 | 0.935 | 0.9912 | OPEN LINE FROM BUS 184652 [BROSD2 315.00] TO BUS 184653 [BRO315 A315.00] CKT 1
184756 ROUVD1 230.00 | 0.947 | 0.9547 | OPEN LINE FROM BUS 180717 [JCA735 735.00] TO BUS 180730 [CAR735 735.00] CKT 1
184757 ROUVD2 230.00 | 0.9474 | 0.955 | OPEN LINE FROM BUS 180717 [JCA735 735.00] TO BUS 180730 [CAR735 735.00] CKT 1
184800 SIDBEC 230.00 | 0.9158 | 0.9463 | OPEN LINE FROM BUS 182030 [CAR230 230.00] TO BUS 184800 [SIDBEC 230.00] CKT 1
184818 DSORES 230.00 | 0.9221 | 0.9473 | OPEN LINE FROM BUS 180730 [CAR735 735.00] TO BUS 182030 [CAR230 230.00] CKT 2
184844 DGYEAR 120.00 | 0.9357 | 0.9643 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184879 DSTELC 230.00 | 0.917 | 0.9473 | OPEN LINE FROM BUS 182001 [BCV230 230.00] TO BUS 184879 [DSTELC 230.00] CKT 1
185740 +ROBBE1-120E120.00 | 1.0515 | 1.0411 | OPEN LINE FROM BUS 180703 [LEV735 735.00] TO BUS 180705 [MAN735 735.00] CKT &3
185780 CLAIRE 120.00 | 1.057 | 1.0248 | OPEN LINE FROM BUS 180703 [LEV735 735.00] TO BUS 180705 [MAN735 735.00] CKT &3
186368 NORDA2 230.00 | 1.0528 | 1.0417 | OPEN LINE FROM BUS 182201 [GOE230 230.00] TO BUS 181601 [GOE161 161.00] CKT 12
186373 DNORD2 230.00 | 1.0528 | 1.0417 | OPEN LINE FROM BUS 182201 [GOE230 230.00] TO BUS 181601 [GOE161 161.00] CKT 12
186410 ANSEVA 161.00 | 1.0806 | 1.0772 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
186411 DANSEV 161.00 | 1.0804 | 1.0771 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
186430 LACALF1-315E315.00 | 1.0563 | 1.0464 | OPEN LINE FROM BUS 186460 [LEPLAT1-315E315.00] TO BUS 186461 [LEPLAT1-315D315.00] CKT 1
186431 LACALF1-315D315.00 | 1.054 | 1.042 | OPEN LINE FROM BUS 186460 [LEPLAT1-315E315.00] TO BUS 186461 [LEPLAT1-315D315.00] CKT 1
186460 LEPLAT1-315E315.00 | 1.0507 | 1.0333 | OPEN LINE FROM BUS 186460 [LEPLAT1-315E315.00] TO BUS 186462 [LEPLAT1--35E34.500] CKT 1
186461 LEPLAT1-315D315.00 | 1.0507 | 1.0332 | OPEN LINE FROM BUS 186460 [LEPLAT1-315E315.00] TO BUS 186462 [LEPLAT1--35E34.500] CKT 1
186580 VIGDEN1-120E120.00 | 1.0504 | 1.0365 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
186581 VIGDEN1-120D120.00 | 1.0503 | 1.0365 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
186777 DANSP 230.00 | 1.0965 | 1.0884 | OPEN LINE FROM BUS 182201 [GOE230 230.00] TO BUS 181601 [GOE161 161.00] CKT 12
186790 RENARD 161.00 | 1.0637 | 1.0594 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
186945 ECARLE 230.00 | 1.0551 | 1.0431 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
186946 DCARLE 230.00 | 1.0529 | 1.0409 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
186970 MTLOUI 230.00 | 1.0949 | 1.0869 | OPEN LINE FROM BUS 182201 [GOE230 230.00] TO BUS 181601 [GOE161 161.00] CKT 12
186975 GROSMO 230.00 | 1.0974 | 1.0894 | OPEN LINE FROM BUS 182201 [GOE230 230.00] TO BUS 181601 [GOE161 161.00] CKT 12
186976 DMTLOUIS 230.00 | 1.0949 | 1.0868 | OPEN LINE FROM BUS 182201 [GOE230 230.00] TO BUS 181601 [GOE161 161.00] CKT 12
186980 MONTSE 161.00 | 1.0878 | 1.085 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
187201 LANGE1 315.00 | 0.9392 | 1.0039 | OPEN LINE FROM BUS 187201 [LANGE1 315.00] TO BUS 187203 [DLANG1 315.00] CKT 1
187208 MTLEST 315.00 | 0.8998 | 0.9969 | OPEN LINE FROM BUS 187207 [MTLESD A315.00] TO BUS 187208 [MTLEST 315.00] CKT 1
187328 DELOR315-2 315.00 | 1.0514 | 0.9918 | OPEN LINE FROM BUS 180463 [VIG315 315.00] TO BUS 187328 [DELOR315-2 315.00] CKT 1
188225 DORION 120.00 | 0.9437 | 0.9714 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
188406 DJOLY1 120.00 | 1.06 | 1.0445 | OPEN LINE FROM BUS 154073 [IPB_MAS_JA42220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
188407 DJOLY2 120.00 | 1.0543 | 1.0392 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
188411 DLANN1 120.00 | 1.0813 | 1.0638 | OPEN LINE FROM BUS 154072 [IPB_MAS_JA41220.00] TO BUS 180526 [OUTHAW 220.00] CKT 1
188412 DLANN2 120.00 | 1.0741 | 1.057 | OPEN LINE FROM BUS 154050 [HAWTHORNE_TS220.00] TO BUS 154073 [IPB_MAS_JA42220.00] CKT 1
188630 ALPHA 120.00 | 1.058 | 1.0355 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
188631 DALPH1 120.00 | 1.0583 | 1.0358 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
188632 DALPH2 120.00 | 1.0583 | 1.0358 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
188795 JOLIET 120.00 | 1.0582 | 1.0358 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
189225 PER<B> 735.00 | 1.0557 | 1.0449 | OPEN LINE FROM BUS 180703 [LEV735 735.00] TO BUS 180704 [LTD735 735.00] CKT 1
190001 BEECHW 138.00 | 1.0505 | 1.0381 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190003 GRFALL 138.00 | 1.0732 | 1.0354 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190005 GRFLEAST 138.00 | 1.0733 | 1.0354 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190011 NEWCST 138.00 | 1.0506 | 1.0326 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190028 111144 138.00 | 1.0582 | 1.0357 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190072 IROQT1 138.00 | 1.091 | 1.0321 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190072 IROQT1 138.00 | 0.948 | 1.0321 | OPEN LINE FROM BUS 190419 [EDMSTN 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
190082 KESWICK 230.00 | 1.0659 | 1.0494 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190110 REPAP1 138.00 | 1.0504 | 1.0324 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190113 T1118APP 138.00 | 1.0508 | 1.0327 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190161 110553 138.00 | 1.0501 | 1.0356 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190179 11401214 138.00 | 1.0911 | 1.0323 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190179 11401214 138.00 | 0.9488 | 1.0323 | OPEN LINE FROM BUS 190419 [EDMSTN 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
190190 MIRPSN 138.00 | 1.0508 | 1.0327 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190199 SALBRY 230.00 | 1.0812 | 0.9927 | OPEN LINE FROM BUS 190199 [SALBRY 230.00] TO BUS 190200 [SALBRY 138.00] CKT 1
190294 HIGHBANK 230.00 | 1.0523 | 1.0337 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190296 T2131GAS 230.00 | 1.0522 | 1.0335 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190310 STANDR 138.00 | 1.079 | 1.037 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190332 NEWCST 230.00 | 1.0526 | 1.0342 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190357 T1140L17 138.00 | 1.0747 | 1.0349 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190362 MCCNGF 138.00 | 1.0743 | 1.0344 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190403 117562 138.00 | 1.0734 | 1.0355 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190410 EDMSTN 138.00 | 1.0955 | 1.0333 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190411 IROQT2 138.00 | 1.0883 | 1.0277 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190419 EDMSTN 345.00 | 1.1037 | 1.0315 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190420 STANDR 345.00 | 1.0805 | 1.0292 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190426 114084 138.00 | 1.0913 | 1.0323 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190447 T1110QTN 138.00 | 1.0656 | 1.0284 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190448 STQNTN 138.00 | 1.0654 | 1.0282 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190475 FRSEDM 138.00 | 1.0842 | 1.0236 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190479 STBASI 138.00 | 1.0911 | 1.0323 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190510 1186TAP 138.00 | 1.0505 | 1.0325 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190511 SWEENL138 138.00 | 1.0504 | 1.0324 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190513 T1118CHA 138.00 | 1.0508 | 1.0326 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190619 EDMN345 345.00 | 1.1037 | 1.0315 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190985 BORDER-5 138.00 | 1.0516 | 1.0384 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190986 TINKER-1 138.00 | 1.0572 | 1.0349 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190988 FLOS INN 138.00 | 1.0529 | 1.0384 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2

## MISO_N-1_VOLTAGE_SUM
BUS | VCONT | VINIT | CONTINGENCY | COMMENTS
249891 08BRWNSB 138.00 | 0.9367 | 0.9482 | OPEN LINE FROM BUS 249500 [08AMO 345.00] TO BUS 250240 [08AMO69 69.000] CKT 1
249892 08AVONEA 138.00 | 0.9391 | 0.9506 | OPEN LINE FROM BUS 249500 [08AMO 345.00] TO BUS 250240 [08AMO69 69.000] CKT 1
264658 19SANDU 120.00 | 0.794 | 1.0316 | OPEN LINE FROM BUS 265077 [19BANNER 345.00] TO BUS 265088 [19BANNER 120.00] CKT 1
264830 19STCPP 220.00 | 1.0604 | 1.0602 | OPEN LINE FROM BUS 264706 [19GRNEC 345.00] TO BUS 264865 [19GRNEC 26.000] CKT 1 | Connected to IESO system, IESO planning criteria should be applied.
265088 19BANNER 120.00 | 0.794 | 1.0359 | OPEN LINE FROM BUS 265077 [19BANNER 345.00] TO BUS 265088 [19BANNER 120.00] CKT 1
334436 6P AC BK% 230.00 | 0.9274 | 0.964 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334437 6KOLBS% 230.00 | 0.9187 | 0.9672 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334438 6HANKS 230.00 | 0.9186 | 0.9698 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334444 6KEITHLAKE% 230.00 | 0.9255 | 0.9622 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334445 6SOSIDE! 230.00 | 0.9264 | 0.963 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334446 6SLTGRAS! 230.00 | 0.9267 | 0.9633 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334447 6VALSOUTH! 230.00 | 0.9267 | 0.9633 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
336003 6DNLDVL 230.00 | 0.9232 | 0.9808 | OPEN LINE FROM BUS 336001 [6EVGREN! 230.00] TO BUS 336003 [6DNLDVL 230.00] CKT 1
336004 6BYVRET! 230.00 | 0.9235 | 0.9758 | OPEN LINE FROM BUS 336001 [6EVGREN! 230.00] TO BUS 336003 [6DNLDVL 230.00] CKT 1
336005 6WELCOM! 230.00 | 0.928 | 0.9757 | OPEN LINE FROM BUS 336001 [6EVGREN! 230.00] TO BUS 336003 [6DNLDVL 230.00] CKT 1
337353 4RINGGOLD_LA138.00 | 0.9337 | 0.9913 | OPEN LINE FROM BUS 500140 [CARROLL6 230.00] TO BUS 500150 [CARROLL4 138.00] CKT 1
337555 3T.E.P/S-F 115.00 | 0.9384 | 1.013 | OPEN LINE FROM BUS 337561 [8EL DORADO% 500.00] TO BUS 337539 [3EL DORADO! 115.00] CKT 1
338651 3SUMMERVLLE#115.00 | 0.9376 | 1.013 | OPEN LINE FROM BUS 337561 [8EL DORADO% 500.00] TO BUS 337539 [3EL DORADO! 115.00] CKT 1
347783 4MTC DVST 138.00 | 0.9378 | 0.974 | OPEN LINE FROM BUS 249510 [08GIBSON 345.00] TO BUS 346508 [7ALBION 345.00] CKT 1
500280 ELEESV 6 230.00 | 0.9255 | 0.9923 | OPEN LINE FROM BUS 500280 [ELEESV 6 230.00] TO BUS 500770 [RODEMR 6 230.00] CKT 1
500470 LEESV 6 230.00 | 0.933 | 0.9937 | OPEN LINE FROM BUS 500280 [ELEESV 6 230.00] TO BUS 500770 [RODEMR 6 230.00] CKT 1
500762 REDRVRTAP4 138.00 | 0.9366 | 1.0067 | OPEN LINE FROM BUS 500140 [CARROLL6 230.00] TO BUS 500150 [CARROLL4 138.00] CKT 1
502401 FLANDER6 230.00 | 0.9397 | 0.9836 | OPEN LINE FROM BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1
502402 ACADIAN6 230.00 | 0.9392 | 0.986 | OPEN LINE FROM BUS 502402 [ACADIAN6 230.00] TO BUS 502403 [BONIN 6 230.00] CKT 1
502417 ELKS 6 230.00 | 0.901 | 0.9792 | OPEN LINE FROM BUS 502417 [ELKS 6 230.00] TO BUS 502425 [BEADLE 6 230.00] CKT 1
502425 BEADLE 6 230.00 | 0.9193 | 0.9809 | OPEN LINE FROM BUS 502401 [FLANDER6 230.00] TO BUS 502425 [BEADLE 6 230.00] CKT 1
601001 FORBES 2 500.00 | 1.0589 | 1.0211 | OPEN LINE FROM BUS 601016 [CHIS CO2 500.00] TO BUS 601017 [CHIS-N 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
601012 ROSEAUN2 500.00 | 1.1343 | 1.095 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
601013 ROSEAUS2 500.00 | 1.1343 | 1.0436 | OPEN LINE FROM BUS 601013 [ROSEAUS2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
601017 CHIS-N 2 500.00 | 1.1032 | 0.9994 | OPEN LINE FROM BUS 601016 [CHIS CO2 500.00] TO BUS 601017 [CHIS-N 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
601038 ROSEAUM 2 500.00 | 1.1343 | 1.0626 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
603284 ODELL WIND 7115.00 | 1.0682 | 1.0616 | OPEN LINE FROM BUS 601032 [FIELD_S3 345.00] TO BUS 601033 [FIELD_N3 345.00] CKT 1
603285 WOAD HILL 7 115.00 | 1.0672 | 1.0605 | OPEN LINE FROM BUS 601032 [FIELD_S3 345.00] TO BUS 601033 [FIELD_N3 345.00] CKT 1
620214 BIGSTON7 115.00 | 1.0613 | 1.0349 | OPEN LINE FROM BUS 620314 [BIGSTON4 230.00] TO BUS 620315 [BIGSTN1G 24.000] CKT 1
631221 BEVERLY3 345.00 | 0.9146 | 0.998 | OPEN LINE FROM BUS 631148 [MORGANV3 345.00] TO BUS 631221 [BEVERLY3 345.00] CKT 1
652397 VFODNES7 115.00 | 0.9289 | 0.9903 | OPEN LINE FROM BUS 652398 [VFODNES4 230.00] TO BUS 652397 [VFODNES7 115.00] TO BUS 652396 [VFODNS19 12.500] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
652418 DKSN-ND7 115.00 | 0.8837 | 0.9866 | OPEN LINE FROM BUS 652417 [DICKNSN4 230.00] TO BUS 652418 [DKSN-ND7 115.00] TO BUS 659197 [DICKNSON 913.800] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659120 BRDLAND3 345.00 | 1.0611 | 1.0095 | OPEN LINE FROM BUS 659120 [BRDLAND3 345.00] TO BUS 659205 [BRDLAND4 230.00] TO BUS 659204 [BROADLAND 913.800] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659205 BRDLAND4 230.00 | 1.0607 | 1.0119 | OPEN LINE FROM BUS 652514 [HURON 4 230.00] TO BUS 659205 [BRDLAND4 230.00] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659255 SXF 6 MI RD7115.00 | 0.9034 | 0.9667 | OPEN LINE FROM BUS 652398 [VFODNES4 230.00] TO BUS 652397 [VFODNES7 115.00] TO BUS 652396 [VFODNS19 12.500] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659256 SXF 57TH ST7115.00 | 0.904 | 0.9672 | OPEN LINE FROM BUS 652398 [VFODNES4 230.00] TO BUS 652397 [VFODNES7 115.00] TO BUS 652396 [VFODNS19 12.500] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659257 SXF SHINDLR7115.00 | 0.9047 | 0.9679 | OPEN LINE FROM BUS 652398 [VFODNES4 230.00] TO BUS 652397 [VFODNES7 115.00] TO BUS 652396 [VFODNS19 12.500] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659258 SXF HARSBRG7115.00 | 0.913 | 0.9756 | OPEN LINE FROM BUS 652398 [VFODNES4 230.00] TO BUS 652397 [VFODNES7 115.00] TO BUS 652396 [VFODNS19 12.500] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659259 SXF CHANCLR7115.00 | 0.9276 | 0.9891 | OPEN LINE FROM BUS 652398 [VFODNES4 230.00] TO BUS 652397 [VFODNES7 115.00] TO BUS 652396 [VFODNS19 12.500] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659420 ANTELOP-LNX3345.00 | 1.0882 | 1.02 | OPEN LINE FROM BUS 659101 [ANTELOP3 345.00] TO BUS 659420 [ANTELOP-LNX3345.00] CKT Z | WAPA violation: MISO doesn't have a topology update to provide.
659421 BRDLAND-LNX3345.00 | 1.0611 | 1.0095 | OPEN LINE FROM BUS 659120 [BRDLAND3 345.00] TO BUS 659421 [BRDLAND-LNX3345.00] CKT Z | WAPA violation: MISO doesn't have a topology update to provide.
659424 LELAND2-LNX3345.00 | 1.0889 | 1.0203 | OPEN LINE FROM BUS 659105 [LELANDO3 345.00] TO BUS 659424 [LELAND2-LNX3345.00] CKT Z | WAPA violation: MISO doesn't have a topology update to provide.
661008 BEULAH 7 115.00 | 0.9342 | 1.016 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661018 COYOTE 7 115.00 | 0.9439 | 1.0168 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661019 MATHSON7 115.00 | 0.8847 | 0.9858 | OPEN LINE FROM BUS 652417 [DICKNSN4 230.00] TO BUS 652418 [DKSN-ND7 115.00] TO BUS 659197 [DICKNSON 913.800] CKT 1 | Coveredy by Coyote Continuity SPS
661020 DIXGREENRVR7115.00 | 0.8893 | 0.9838 | OPEN LINE FROM BUS 652417 [DICKNSN4 230.00] TO BUS 652418 [DKSN-ND7 115.00] TO BUS 659197 [DICKNSON 913.800] CKT 1 | Coveredy by Coyote Continuity SPS
661021 WSTMD1 7 115.00 | 0.9353 | 1.0144 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661022 DICKNTH7 115.00 | 0.8808 | 0.9798 | OPEN LINE FROM BUS 652417 [DICKNSN4 230.00] TO BUS 652418 [DKSN-ND7 115.00] TO BUS 659197 [DICKNSON 913.800] CKT 1 | Coveredy by Coyote Continuity SPS
661024 WDICKSN7 115.00 | 0.8801 | 0.9806 | OPEN LINE FROM BUS 652417 [DICKNSN4 230.00] TO BUS 652418 [DKSN-ND7 115.00] TO BUS 659197 [DICKNSON 913.800] CKT 1 | Coveredy by Coyote Continuity SPS
661040 MCLGHLN7 115.00 | 0.9362 | 0.9659 | OPEN LINE FROM BUS 661038 [GLENHAM4 230.00] TO BUS 661035 [GLENHAM7 115.00] TO BUS 661600 [GLENHAM9 41.600] CKT 2
661041 MCINTSH7 115.00 | 0.9367 | 0.9665 | OPEN LINE FROM BUS 661038 [GLENHAM4 230.00] TO BUS 661035 [GLENHAM7 115.00] TO BUS 661600 [GLENHAM9 41.600] CKT 2
661070 N ENGLN7 115.00 | 0.929 | 0.9941 | OPEN LINE FROM BUS 652417 [DICKNSN4 230.00] TO BUS 652418 [DKSN-ND7 115.00] TO BUS 659197 [DICKNSON 913.800] CKT 1
667061 MINTS 4 230.00 | 0.9355 | 0.9988 | OPEN LINE FROM BUS 667028 [GR.RPDS4 230.00] TO BUS 667029 [ASHERN 4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667062 VERMIL 4 230.00 | 0.9291 | 0.9968 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667064 RAVLAKE4 230.00 | 0.8376 | 0.966 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667065 BIRTLE 4 230.00 | 0.8223 | 0.965 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667066 VIRDN W4 230.00 | 0.7985 | 0.9604 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667067 RESTON 4 230.00 | 0.803 | 0.9698 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667068 SOURENB4 230.00 | 0.8768 | 0.9745 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667069 SOURSTP4 230.00 | 0.8779 | 0.9756 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667070 CORNWLS4 230.00 | 0.9086 | 0.9788 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667071 NEEPAWA4 230.00 | 0.9483 | 0.9839 | OPEN LINE FROM BUS 667053 [PORTSOU4 230.00] TO BUS 667070 [CORNWLS4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667072 WHTSL2 4 220.00 | 1.1166 | 1.1141 | OPEN LINE FROM BUS 601016 [CHIS CO2 500.00] TO BUS 601017 [CHIS-N 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667073 WHTSL1 4 220.00 | 1.1166 | 1.1141 | OPEN LINE FROM BUS 601016 [CHIS CO2 500.00] TO BUS 601017 [CHIS-N 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667232 KEEYASK6 138.80 | 1.0714 | 1.0678 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667247 KEEY_1-2_6 138.80 | 1.0696 | 1.0665 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667248 KEEY_3_6 138.80 | 1.0696 | 1.0665 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667249 KEEY_4_6 138.80 | 1.0695 | 1.0664 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667250 KEEY_5_6 138.80 | 1.0705 | 1.0671 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667251 KEEY_6-7_6 138.80 | 1.0705 | 1.0671 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667301 POINTDB7 110.00 | 1.1214 | 1.1212 | OPEN LINE FROM BUS 601013 [ROSEAUS2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667302 SLAVEFL7 110.00 | 1.1185 | 1.118 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
667302 SLAVEFL7 110.00 | 1.1185 | 1.118 | OPEN LINE FROM BUS 601013 [ROSEAUS2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668015 MR11 T 7 110.00 | 0.9276 | 1.0089 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668016 RAPDCTY7 110.00 | 0.93 | 1.0101 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668017 BRANE 7 110.00 | 0.938 | 1.0147 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668018 HIGHLND7 110.00 | 0.9312 | 1.0086 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668019 FORTIER7 110.00 | 0.9273 | 1.0049 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668020 CROCUSP7 110.00 | 0.931 | 1.0083 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668021 BD52-TP7 110.00 | 0.9371 | 1.0139 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668022 BRANDON7 110.00 | 0.9397 | 1.0162 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668023 BE1 TP 7 110.00 | 0.9396 | 1.0161 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668024 KOCHB2 7 110.00 | 0.939 | 1.0156 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668025 KOCHB1 7 110.00 | 0.9391 | 1.0157 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668026 BK41-TP7 110.00 | 0.9335 | 1.0106 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668027 MAPLELF7 110.00 | 0.9375 | 1.0142 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668028 CANEXUS7 110.00 | 0.9305 | 1.0079 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668030 MINDOS 7 110.00 | 0.9308 | 1.0109 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668047 LAVEREN7 110.00 | 1.0637 | 1.063 | OPEN LINE FROM BUS 667047 [LAVEREN4 230.00] TO BUS 667048 [LETELER4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668049 PF-BK8 7 110.00 | 1.0778 | 1.0771 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668050 PINEFLS7 110.00 | 1.0778 | 1.0771 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668051 GULL LK7 110.00 | 1.064 | 1.0629 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668052 PA2-TAP7 110.00 | 1.0778 | 1.0771 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668053 ABIT-1 7 110.00 | 1.0778 | 1.0771 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668057 PA1-TAP7 110.00 | 1.0778 | 1.0771 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668058 ABIT-2 7 110.00 | 1.0778 | 1.0771 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668061 PF-BK7 7 110.00 | 1.0779 | 1.0771 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668062 GREATFL7 110.00 | 1.0883 | 1.0877 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668064 RAVLAKE7 110.00 | 0.9121 | 0.9967 | OPEN LINE FROM BUS 667064 [RAVLAKE4 230.00] TO BUS 668064 [RAVLAKE7 110.00] TO BUS 669143 [RAVLKB39 13.800] CKT 3 | MH violation: MISO doesn't have an update to provide
668070 CORNW1 7 110.00 | 0.9399 | 1.0164 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668071 CORNW3 7 110.00 | 0.9399 | 1.0164 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668072 CORNW427 110.00 | 0.9399 | 1.0164 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668075 LACDUBN7 110.00 | 1.0812 | 1.081 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668076 BEAUSJ 7 110.00 | 1.0756 | 1.0755 | OPEN LINE FROM BUS 608410 [WARRVRN2 500.00] TO BUS 608411 [WARRVRM2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668077 SG12 TP7 110.00 | 1.0808 | 1.0807 | OPEN LINE FROM BUS 602013 [ROSEAU 4 230.00] TO BUS 657757 [MORANVI4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668078 MCARTHR7 110.00 | 1.0844 | 1.0842 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668079 MCARTH27 110.00 | 1.0844 | 1.0842 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668080 MCARTH17 110.00 | 1.0843 | 1.0841 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668081 7SISTER7 110.00 | 1.082 | 1.082 | BASE CASE | MH violation: MISO doesn't have an update to provide
668082 SR3SW3T7 110.00 | 1.082 | 1.082 | BASE CASE | MH violation: MISO doesn't have an update to provide
668083 SK1 TP7 110.00 | 1.0818 | 1.0816 | OPEN LINE FROM BUS 667073 [WHTSL1 4 220.00] TO BUS 668091 [WHSL1PH7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide
668084 SK1 SUB7 110.00 | 1.1545 | 1.1544 | OPEN LINE FROM BUS 667072 [WHTSL2 4 220.00] TO BUS 668092 [WHSL2PH7 110.00] CKT 8 | MH violation: MISO doesn't have an update to provide
668085 BRERTON7 110.00 | 1.1534 | 1.1532 | OPEN LINE FROM BUS 667073 [WHTSL1 4 220.00] TO BUS 668091 [WHSL1PH7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide
668086 STAR LK7 110.00 | 1.1513 | 1.1511 | OPEN LINE FROM BUS 667073 [WHTSL1 4 220.00] TO BUS 668091 [WHSL1PH7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide
668089 VIVIAN 7 110.00 | 1.0648 | 1.0631 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668090 WHITESH7 110.00 | 1.0814 | 1.081 | OPEN LINE FROM BUS 667073 [WHTSL1 4 220.00] TO BUS 668091 [WHSL1PH7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide
668091 WHSL1PH7 110.00 | 1.0814 | 1.0715 | OPEN LINE FROM BUS 667073 [WHTSL1 4 220.00] TO BUS 668091 [WHSL1PH7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide
668092 WHSL2PH7 110.00 | 1.0814 | 1.0715 | OPEN LINE FROM BUS 667072 [WHTSL2 4 220.00] TO BUS 668092 [WHSL2PH7 110.00] CKT 8 | MH violation: MISO doesn't have an update to provide
668116 YV5-TP 7 110.00 | 1.0608 | 1.0601 | OPEN LINE FROM BUS 667029 [ASHERN 4 230.00] TO BUS 667030 [SILVRTP4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide
668149 SEDDONS7 110.00 | 1.0784 | 1.0783 | OPEN LINE FROM BUS 601001 [FORBES 2 500.00] TO BUS 601017 [CHIS-N 2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide
672602 BDX 4 230.00 | 1.1944 | 1.0941 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672602 [BDX 4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672607 REGINA 4 230.00 | 1.0804 | 1.0747 | OPEN LINE FROM BUS 672607 [REGINA 4 230.00] TO BUS 672608 [FLEETST4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672608 FLEETST4 230.00 | 1.0763 | 1.0705 | OPEN LINE FROM BUS 672608 [FLEETST4 230.00] TO BUS 672408 [FLEETST8 72.000] CKT 1 | SPC violation: MISO doesn't have an update to provide
672609 KENNEDY4 230.00 | 1.0594 | 1.0544 | OPEN LINE FROM BUS 672611 [WHWO-TAP 230.00] TO BUS 672614 [TANTALL4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672610 POPLAR 4 230.00 | 1.0913 | 1.0913 | BASE CASE | SPC violation: MISO doesn't have an update to provide
672612 CONDIE 4 230.00 | 1.0804 | 1.0724 | OPEN LINE FROM BUS 672642 [QE 3 4 230.00] TO BUS 672540 [QE 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672613 AUBURNT4 230.00 | 1.0631 | 1.0089 | OPEN LINE FROM BUS 667067 [RESTON 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672613 AUBURNT4 230.00 | 0.7698 | 1.0089 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672616 PEEBLES4 230.00 | 1.0864 | 1.0685 | OPEN LINE FROM BUS 672609 [KENNEDY4 230.00] TO BUS 672616 [PEEBLES4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672617 KEND-TAP 230.00 | 1.0858 | 1.0736 | OPEN LINE FROM BUS 672609 [KENNEDY4 230.00] TO BUS 672616 [PEEBLES4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672621 SHAND 4 230.00 | 1.0913 | 1.0913 | BASE CASE | SPC violation: MISO doesn't have an update to provide
672630 EBCAMPB4 230.00 | 1.078 | 1.078 | BASE CASE | SPC violation: MISO doesn't have an update to provide
672635 BETHUNETAP 230.00 | 1.0786 | 1.0687 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672636 BETHUNE 230.00 | 1.0784 | 1.0685 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672638 BEATTY 4 230.00 | 1.0699 | 1.0666 | OPEN LINE FROM BUS 672650 [NIPAWIN4 230.00] TO BUS 672352 [NIPAWI3G 13.800] CKT 1 | SPC violation: MISO doesn't have an update to provide
672642 QE 3 4 230.00 | 1.1284 | 1.0496 | OPEN LINE FROM BUS 672642 [QE 3 4 230.00] TO BUS 672540 [QE 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672649 CODETTE4 230.00 | 1.0846 | 1.084 | OPEN LINE FROM BUS 672630 [EBCAMPB4 230.00] TO BUS 672649 [CODETTE4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672650 NIPAWIN4 230.00 | 1.087 | 1.087 | BASE CASE | SPC violation: MISO doesn't have an update to provide
672651 MAIDNORTH 230.00 | 1.0706 | 1.0666 | OPEN LINE FROM BUS 672651 [MAIDNORTH 230.00] TO BUS 672696 [BRADA 4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672656 NEWBPSS 230.00 | 1.0773 | 1.0683 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672664 ROWATT 230.00 | 1.0816 | 1.0761 | OPEN LINE FROM BUS 672607 [REGINA 4 230.00] TO BUS 672608 [FLEETST4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672666 LLOYDMI4 230.00 | 1.075 | 1.075 | BASE CASE | SPC violation: MISO doesn't have an update to provide
672670 COTEAU 4 230.00 | 1.0861 | 1.062 | OPEN LINE FROM BUS 672670 [COTEAU 4 230.00] TO BUS 672570 [COTEAU 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672682 LIEB-TAP 230.00 | 1.0805 | 1.0718 | OPEN LINE FROM BUS 672685 [SWIFTCU4 230.00] TO BUS 672585 [SWIFTCU6 138.00] CKT 2 | SPC violation: MISO doesn't have an update to provide
672683 MCNEILL4 230.00 | 1.0813 | 1.0726 | OPEN LINE FROM BUS 672685 [SWIFTCU4 230.00] TO BUS 672585 [SWIFTCU6 138.00] CKT 2 | SPC violation: MISO doesn't have an update to provide
672684 RUSHLAK4 230.00 | 1.1009 | 1.0781 | OPEN LINE FROM BUS 672684 [RUSHLAK4 230.00] TO BUS 672685 [SWIFTCU4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672685 SWIFTCU4 230.00 | 1.0736 | 1.0652 | OPEN LINE FROM BUS 672685 [SWIFTCU4 230.00] TO BUS 672585 [SWIFTCU6 138.00] CKT 2 | SPC violation: MISO doesn't have an update to provide
672686 ASSINIB4 230.00 | 1.0984 | 1.0896 | OPEN LINE FROM BUS 672684 [RUSHLAK4 230.00] TO BUS 672685 [SWIFTCU4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672688 PASQUA 4 230.00 | 1.0812 | 1.0698 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
672697 ML EAST4 230.00 | 1.0721 | 1.0111 | OPEN LINE FROM BUS 672697 [ML EAST4 230.00] TO BUS 672698 [ML NRTH4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
673601 KSY SUB TAP 230.00 | 1.0943 | 1.0801 | OPEN LINE FROM BUS 672616 [PEEBLES4 230.00] TO BUS 673601 [KSY SUB TAP 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide
673602 KISBEY SUB S230.00 | 1.0935 | 1.0793 | OPEN LINE FROM BUS 672616 [PEEBLES4 230.00] TO BUS 673601 [KSY SUB TAP 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide

## PJM_N-1_VOLTAGE_SUM
BUS | VCONT | VINIT | CONTINGENCY
94150 VFT ENJECT 230.00 | 1.0702 | 1.0071 | L_D-2256
128819 HDSN_NONFIRM345.00 | 1.0598 | 1.0527 | L_V-2301
200521 26SAXTON 115.00 | 0.9132 | 0.9948 | B2-PN-115-079
200526 26THRE SPR 115.00 | 0.9061 | 0.9885 | B2-PN-115-079
200584 26GRANDVW 115.00 | 0.9217 | 1.0124 | B3-PN-115-068
200587 26CLRK SUM 115.00 | 0.908 | 1.0095 | B3-PN-115-068
200632 26ERIE WST 115.00 | 1.0582 | 1.0389 | B2-PN-345-002
200647 26FOREST 115.00 | 1.0547 | 1.0412 | B2-PN-115-026
200739 26SHELOCTA 115.00 | 1.0524 | 1.0392 | B2-PN-115-061
200818 26WARREN 2 115.00 | 1.0511 | 1.0381 | B2-PN-115-115
200930 26MAINESBURG345.00 | 1.0561 | 1.0468 | B2-TIE-345-104
204529 27GERMANTN 115.00 | 1.0697 | 1.0195 | B2-ME-115-009
204538 27STRABAN 115.00 | 1.0559 | 1.013 | B3-ME-115-008
204619 27PORTLND 115.00 | 1.0585 | 1.0418 | B2-ME-115-030
204702 27MIDDCRK 69.000 | 0.915 | 0.9816 | B2-ME-230-003
204781 27TURFCLUB 69.000 | 0.9168 | 0.9832 | B2-MEL-69-012
204826 27CONTY LN 69.000 | 0.9201 | 0.9882 | B2-ME-230-003
204852 27RNGROCKS 69.000 | 0.9143 | 0.9803 | B2-ME-230-003
207973 FRAC 230.00 | 1.0556 | 1.0425 | PL100142
207974 FRAC TR2 230.00 | 1.0553 | 1.0423 | PL100142
207975 FRAC TR3 230.00 | 1.0555 | 1.0424 | PL100142
208004 JUNI BU1 230.00 | 1.0596 | 1.0495 | PL100598
208006 JUNI CAP 230.00 | 1.0606 | 1.0503 | PL100598
208301 DILL 1 138.00 | 0.8962 | 0.9894 | 208375(EPET 1)-208676(PACI 1)_1
208305 DNLY 1 138.00 | 0.6551 | 0.9922 | 208497(LAPR TP1)-208743(RTWN 1)_1
208308 DNLY 138.00 | 0.655 | 0.9922 | 208497(LAPR TP1)-208743(RTWN 1)_1
208676 PACI 1 138.00 | 0.8959 | 0.9897 | 208375(EPET 1)-208676(PACI 1)_1
208694 PRIN WH1 138.00 | 0.6605 | 0.9913 | 208497(LAPR TP1)-208743(RTWN 1)_1
208700 PRINUGW1 138.00 | 0.6563 | 0.992 | 208497(LAPR TP1)-208743(RTWN 1)_1
208743 RTWN 1 138.00 | 0.6547 | 0.9931 | 208497(LAPR TP1)-208743(RTWN 1)_1
208843 TWVA 2 69.000 | 0.8773 | 0.9499 | PL101330
209780 CARL TP4 69.000 | 0.6961 | 1.0008 | PL101421
209781 CARL 1 69.000 | 1.0379 | 1.0128 | PL101418
209785 CARLUG13 69.000 | 1.0378 | 1.0127 | PL101418
209788 CABA T2 69.000 | 1.0363 | 1.0112 | PL101418
209920 FRY 3 69.000 | 0.6952 | 1.0002 | PL101421
210003 LAPU TP 69.000 | 0.696 | 1.0008 | PL101421
210004 LAPU 69.000 | 0.6955 | 1.0004 | PL101421
210041 MECH 4 69.000 | 0.698 | 1.0022 | PL101421
210043 SMEC 69.000 | 0.5447 | 1.0053 | PL101420
210075 MOAL TP3 69.000 | 0.5492 | 1.0023 | PL101420
210077 MOAL 1 69.000 | 0.5556 | 1.0013 | PL101420
210172 RALS TP 69.000 | 0.6968 | 1.0013 | PL101421
210173 RALS 69.000 | 0.694 | 0.9993 | PL101421
210208 ROSS 3 69.000 | 0.5456 | 1.0029 | PL101420
210325 WCARUG13 69.000 | 1.0378 | 1.0127 | PL101418
210326 WCARTI13 69.000 | 1.0378 | 1.0127 | PL101418
210333 WIGR 69.000 | 1.0211 | 1.0147 | PL100605
211805 PROV 4 69.000 | 0.8218 | 0.9919 | PL101449
211862 SUB2 1 69.000 | 0.8252 | 0.9902 | PL101449
211863 SUBU TP1 69.000 | 0.8252 | 0.9903 | PL101449
212141 FQL1 1 69.000 | 0.8694 | 0.9447 | PL101464
212264 LOHA CTG 69.000 | 0.8746 | 0.9461 | PL101464
213521 CROMBY 138.00 | 1.0704 | 1.0501 | PERK785/* $ MONTCO $ PERK785 $ K
213527 CROMBY1A 69.000 | 1.0594 | 1.0176 | CROM140/* $ CHESCO $ CROM140 $ K
213882 PERKIOM2 138.00 | 1.0655 | 1.0506 | 130-31/* $ MONTCO $ 130-31 $ L
213887 PERKIOMN 138.00 | 1.0749 | 1.0506 | PERK785/* $ MONTCO $ PERK785 $ K
214022 WARRNGTN 230.00 | 1.0505 | 1.0359 | 220-58/* $ MONTCO $ 220-58 $ L
214087 WARRICAP 230.00 | 1.0539 | 1.0392 | 220-58/* $ MONTCO $ 220-58 $ L
214107 PERKICAP 138.00 | 1.0758 | 1.0514 | PERK785/* $ MONTCO $ PERK785 $ K
214111 CROMBCAP 138.00 | 1.0712 | 1.0509 | PERK785/* $ MONTCO $ PERK785 $ K
214199 WARRNGT1 230.00 | 1.0505 | 1.0359 | 220-58/* $ MONTCO $ 220-58 $ L
214200 WARRNGT2 230.00 | 1.0505 | 1.0359 | 220-58/* $ MONTCO $ 220-58 $ L
217178 Q206_HUDSNDC345.00 | 1.0598 | 1.0527 | L_V-2301
218442 G22_VFT230KV230.00 | 1.0702 | 1.0071 | L_D-2256
220410 N.WEST230-3 230.00 | 1.0746 | 1.0138 | BG_CKT2371
220411 N.WEST230-2 230.00 | 1.0749 | 1.0144 | BG_CKT2370
220945 NWEST2CP 230.00 | 1.0775 | 1.0168 | BG_CKT2370
220947 NWEST3CP 230.00 | 1.0772 | 1.0163 | BG_CKT2371
223975 BLU23108 230.00 | 1.0526 | 1.0399 | PP69
224064 HEWTSME 69.000 | 0.8157 | 0.9843 | PP55
224078 HAWK 69 69.000 | 0.9188 | 0.9922 | PP54_B
230900 WY138CAP 138.00 | 1.0704 | 1.06 | CKT 13761/88
230902 WYE69CAP 69.000 | 1.0725 | 1.0646 | CKT 13761/88
231201 BASIN_69 69.000 | 1.07 | 1.0604 | EDGE MR AT20
231208 KIAM_69 69.000 | 1.0729 | 1.0636 | EDGE MR AT20
231216 WEST 69.000 | 1.072 | 1.0628 | EDGE MR AT20
232100 CHURCH 138.00 | 1.0579 | 1.0483 | CKT 6704
232101 WYEMILLS 138.00 | 1.07 | 1.0596 | CKT 13761/88
232102 HILLSBRO 138.00 | 1.0619 | 1.0533 | CKT 23076
232103 STEEL138 138.00 | 1.0589 | 1.0496 | CKT 23076
232107 TOWNSEND 138.00 | 1.0638 | 1.047 | CKT 13808
232112 FELTON 138.00 | 1.0572 | 1.0346 | CKT 13709
232115 EASTON 138.00 | 1.0578 | 1.0509 | CKT 23076
232203 CHURC_69 69.000 | 1.0769 | 1.0627 | CKT 6704
232206 WYE MILL 69.000 | 1.0725 | 1.0646 | CKT 13761/88
232234 TODD 69.000 | 1.0758 | 1.072 | CKT 6702
232235 JACKTOWN 69.000 | 1.0773 | 1.0745 | CKT 6782
232236 E NEWMKT 69.000 | 1.079 | 1.0759 | CKT 6782
232237 CAMBRIDG 69.000 | 1.0769 | 1.0741 | VIENNA AT1
232238 WCAMBRDG 69.000 | 1.0754 | 1.0724 | VIENNA AT2
232275 LORET_69 69.000 | 1.0742 | 1.0508 | CKT 6711
232292 BAYLY 69.000 | 1.076 | 1.0731 | VIENNA AT1
232811 CLOUGH 69.000 | 1.076 | 1.0618 | CKT 6704
232817 ENMKTREA 69.000 | 1.0774 | 1.0743 | CKT 6782
232840 PRIN ANN 69.000 | 1.0734 | 1.05 | CKT 6711
235176 01EMERLD 138.00 | 0.8994 | 0.9883 | B2-WP-138-025
235490 01MORGAN 138.00 | 0.8396 | 0.976 | B2-PE-138-032
235546 01EAGLE 138.00 | 0.9135 | 0.9983 | B2-PE-138-022
238503 02BRIM 69.000 | 1.0955 | 1.0128 | B2-TE-69-009
238522 02RCHLN 69.000 | 0.8955 | 0.9353 | B2-TE-69-029
238881 02LDEQ16 138.00 | 0.8901 | 1.0083 | B2-CEI-138-039
240843 02BG2 69.000 | 0.8999 | 0.9969 | B3-TE-138-002
240886 02NAPOLE 69.000 | 0.8254 | 0.9208 | B2-TE-69-029
240918 02CAMPBL_SP 69.000 | 0.8178 | 0.914 | B2-TE-69-029
242518 05BROADF 500.00 | 1.052 | 1.0444 | 307_B2_TOR9
242519 05CLOVRD 500.00 | 1.0645 | 1.061 | LN 566
242520 05J.FERR 500.00 | 1.0799 | 1.0759 | 307_B2_TOR9
242521 05NAGEL 500.00 | 1.0526 | 1.0494 | 321_B3
242976 05BUCYRC 138.00 | 0.8712 | 0.9931 | 716_B3_05HOWARD 138-1_WOMOAB
243091 05SCALDW 138.00 | 0.8779 | 0.9744 | 608_B3_05MUSKNG 138-1_WOMOAB
243096 05SCUMBL 138.00 | 0.8773 | 0.9695 | 608_B3_05MUSKNG 138-1_WOMOAB
243117 05SULFRS 138.00 | 0.8703 | 0.9956 | 716_B3_05HOWARD 138-1_WOMOAB
243118 05SUMMER 138.00 | 0.8798 | 0.959 | 608_B3_05MUSKNG 138-1_WOMOAB
243123 05SWITZE 138.00 | 0.8924 | 0.9839 | 8893_B2_TOR778A_MOAB
243246 05AUBUNC 138.00 | 0.899 | 0.9799 | 783_B3_05AUBURN 138-1_WOMOAB
243295 05GARRET 138.00 | 0.9045 | 0.9807 | 783_B3_05AUBURN 138-1_WOMOAB
243506 05ELLIOT 138.00 | 0.9138 | 0.9857 | 5940_B2_TOR596
244041 05CLOV 4 69.000 | 1.0643 | 1.0506 | 888_B2_TOR248_WOMOAB
244131 05CLAYTOR 69.000 | 1.0567 | 1.0246 | 229_B3_05MORGAN 138-1_WOMOAB
244133 05INGLES 69.000 | 1.0523 | 1.0174 | 229_B3_05MORGAN 138-1_WOMOAB
244148 05RIVERBEN 69.000 | 1.0521 | 1.0176 | 229_B3_05MORGAN 138-1_WOMOAB
244162 05BYLLESBY 69.000 | 1.0588 | 1.0221 | 194_B2_TOR213_WOMOAB
244594 05CEDARCRK 69.000 | 0.9111 | 1.0018 | 8879_B3_05CEDARC 138-1
244620 05PIKEVL 69.000 | 0.9143 | 0.9929 | 8879_B3_05CEDARC 138-1
244625 05S.PIKEV1 69.000 | 0.9111 | 0.9961 | 8879_B3_05CEDARC 138-1
244640 05S.PIKEV2 69.000 | 0.9111 | 0.9961 | 8879_B3_05CEDARC 138-1
244763 05RIPLEY 69.000 | 0.8637 | 1.0168 | 6048_B2_TOR2844_WOMOAB
245020 05SUMMERFL 69.000 | 0.898 | 0.9778 | 608_B3_05MUSKNG 138-1_WOMOAB
245022 05TE SUMRF 69.000 | 0.8968 | 0.9766 | 608_B3_05MUSKNG 138-1_WOMOAB
245023 05TEBERN 138.00 | 0.8689 | 0.9491 | 608_B3_05MUSKNG 138-1_WOMOAB
245028 05CAPTINA8 69.000 | 0.9193 | 0.9923 | 795_B3_05SOMERT 138-1_MOAB
245084 05CAMERNSS 69.000 | 0.8628 | 0.9581 | 8893_B2_TOR778A_MOAB
245096 05RONDBTM8 69.000 | 0.8571 | 0.9531 | 8893_B2_TOR778A_MOAB
245099 05SWITZER 69.000 | 0.8789 | 0.9725 | 8893_B2_TOR778A_MOAB
245104 05WOODSFLD Z69.000 | 0.8619 | 0.9573 | 8893_B2_TOR778A_MOAB
245108 05POWHAT 8 69.000 | 0.8789 | 0.9725 | 8893_B2_TOR778A_MOAB
245445 05WBYESVLL 69.000 | 0.9185 | 0.9809 | 1046_B3_E CAMBRD 69.0-
245452 05DERWENT 69.000 | 0.9081 | 0.9733 | 608_B3_05MUSKNG 138-1_WOMOAB
245457 05BYESVLLE 69.000 | 0.9137 | 0.9912 | 1046_B3_E CAMBRD 69.0-
245460 05PLSNT C SS69.000 | 0.8967 | 0.9672 | 608_B3_05MUSKNG 138-1_WOMOAB
245472 05S CUMBLN 69.000 | 0.8791 | 0.9675 | 608_B3_05MUSKNG 138-1_WOMOAB
245652 05EAGLECRZ 69.000 | 0.8941 | 1.0177 | 716_B3_05HOWARD 138-1_WOMOAB
245653 05BUCYRS C 69.000 | 0.896 | 1.0179 | 716_B3_05HOWARD 138-1_WOMOAB
245654 05BUCYRUS 69.000 | 0.8944 | 1.0181 | 716_B3_05HOWARD 138-1_WOMOAB
245657 05WSHELBY 69.000 | 0.9034 | 1.0206 | 716_B3_05HOWARD 138-1_WOMOAB
245659 05E BUCYRU 69.000 | 0.8942 | 1.0181 | 716_B3_05HOWARD 138-1_WOMOAB
245661 05GE BUCYR 69.000 | 0.894 | 1.0175 | 716_B3_05HOWARD 138-1_WOMOAB
245663 05HOWARD 69.000 | 0.904 | 1.0275 | 716_B3_05HOWARD 138-1_WOMOAB
245667 05N BUCYRU 69.000 | 0.8943 | 1.0173 | 716_B3_05HOWARD 138-1_WOMOAB
245672 05S GREENW 69.000 | 0.9171 | 1.0063 | 716_B3_05HOWARD 138-1_WOMOAB
245676 05SWAN RUB 69.000 | 0.894 | 1.0175 | 716_B3_05HOWARD 138-1_WOMOAB
245677 05W GALION 69.000 | 0.8979 | 1.022 | 716_B3_05HOWARD 138-1_WOMOAB
245678 05NGALIOSS 69.000 | 0.9015 | 1.0252 | 716_B3_05HOWARD 138-1_WOMOAB
245687 05BROK SWR 69.000 | 0.8987 | 1.0154 | 716_B3_05HOWARD 138-1_WOMOAB
245709 05NEVADA8 69.000 | 0.9174 | 1.0137 | 716_B3_05HOWARD 138-1_WOMOAB
246175 05ABRNCTY1 69.000 | 0.8943 | 0.981 | 783_B3_05AUBURN 138-1_WOMOAB
246177 05ABRNCTY5 69.000 | 0.8981 | 0.9845 | 783_B3_05AUBURN 138-1_WOMOAB
246735 05COOLVL 69.000 | 0.906 | 0.9607 | 6048_B2_TOR2844_WOMOAB
246926 05SENECAVL 69.000 | 0.9081 | 0.9733 | 608_B3_05MUSKNG 138-1_WOMOAB
246958 05BAYER101 69.000 | 1.0527 | 1.0502 | 5729_B2_TOR2233_WOMOAB
247156 05STEAMT 138.00 | 0.8782 | 0.9596 | 608_B3_05MUSKNG 138-1_WOMOAB
247375 05BLUERACER8138.00 | 0.869 | 0.9491 | 608_B3_05MUSKNG 138-1_WOMOAB
247379 05NEVADA SS 69.000 | 0.9174 | 1.0137 | 716_B3_05HOWARD 138-1_WOMOAB
247385 05SAND AV SS69.000 | 0.8941 | 1.0175 | 716_B3_05HOWARD 138-1_WOMOAB
247419 05WINDYHILSS69.000 | 0.8789 | 0.9673 | 608_B3_05MUSKNG 138-1_WOMOAB
247428 05E STREETSS69.000 | 0.894 | 1.0176 | 716_B3_05HOWARD 138-1_WOMOAB
247457 05WOODSFLD8 69.000 | 0.8614 | 0.9569 | 8893_B2_TOR778A_MOAB
247474 05GLENWOOD 69.000 | 0.8952 | 0.9658 | 608_B3_05MUSKNG 138-1_WOMOAB
247490 05RANNELL SS69.000 | 0.8785 | 0.9621 | 608_B3_05MUSKNG 138-1_WOMOAB
247581 W3-111 C 69.000 | 0.8791 | 0.9675 | 608_B3_05MUSKNG 138-1_WOMOAB
247582 W3-112 C 69.000 | 0.8791 | 0.9675 | 608_B3_05MUSKNG 138-1_WOMOAB
247583 W3-113 C 69.000 | 0.8791 | 0.9675 | 608_B3_05MUSKNG 138-1_WOMOAB
247715 05BLUE RACER138.00 | 0.869 | 0.9491 | 608_B3_05MUSKNG 138-1_WOMOAB
247761 05DANFORD SS69.000 | 0.9193 | 0.9923 | 5218_B2_TOR777_WOMOAB
247950 W3-111 E 69.000 | 0.8791 | 0.9675 | 608_B3_05MUSKNG 138-1_WOMOAB
247951 W3-112 E 69.000 | 0.8791 | 0.9675 | 608_B3_05MUSKNG 138-1_WOMOAB
247952 W3-113 E 69.000 | 0.8791 | 0.9675 | 608_B3_05MUSKNG 138-1_WOMOAB
250025 08FLDMN1 138.00 | 0.8781 | 0.954 | P1-#..B2 FOSTER-ENYART 5487
250026 08FLDMN2 138.00 | 0.8781 | 0.954 | P1-#..B2 FOSTER-ENYART 5487
250075 08MTGRY1 138.00 | 0.8526 | 0.9639 | P1-#..B2 FOSTER-ENYART 5487
250076 08MTGRY2 138.00 | 0.8526 | 0.9639 | P1-#..B2 FOSTER-ENYART 5487
250094 08RMNTN1 138.00 | 0.8581 | 0.9533 | P1-#..B2 FOSTER-ENYART 5487
250095 08RMNTN2 138.00 | 0.8581 | 0.9533 | P1-#..B2 FOSTER-ENYART 5487
250142 08WARDSC 138.00 | 0.8666 | 0.9532 | P1-#..B2 FOSTER-ENYART 5487
250150 08ENYART 138.00 | 0.8526 | 0.9667 | P1-#..B2 FOSTER-ENYART 5487
270790 KATYDID ; B345.00 | 1.0533 | 1.0257 | 345-L19601_B-S
270904 TOP CROP ;P1345.00 | 1.0533 | 1.0257 | 345-L19601_B-S
270905 TOP CROP ;P2345.00 | 1.0534 | 1.0258 | 345-L19601_B-S
292421 V3_017_TAP68230.00 | 1.0563 | 1.0449 | V3_017_TAP86-V3-017
292422 V3_017_TAP66230.00 | 1.0556 | 1.0441 | V3_017_TAP86-MORGT230
292423 V3_017_TAP86230.00 | 1.0578 | 1.0434 | V3_017_TAP86-MORGT230
292424 V3_017_TAP84230.00 | 1.0544 | 1.0432 | V3_017_TAP86-V3-017
292630 V3-017 230.00 | 1.0578 | 1.0457 | V3_017_TAP86-V3-017
313819 3ELMFARM 115.00 | 0.9205 | 0.988 | 6OX-3OX
313846 6HARMONY_1 230.00 | 1.0716 | 1.0658 | LN 176
314014 3CANNONB 115.00 | 0.9114 | 1.0091 | LN 2011
314051 3L0MA197 115.00 | 0.9115 | 1.0085 | LN 2011
314112 3IND HIL 115.00 | 0.9287 | 0.9834 | 6BRISTER-3BRISTER
314114 3LINDNDL 115.00 | 0.9216 | 0.984 | 6OX-3OX
314118 3MINNIEV 115.00 | 0.9205 | 0.9854 | 6OX-3OX
314122 3SOWEGO 115.00 | 0.9209 | 0.9945 | 6BRISTER-3BRISTER
314148 3MICR197 115.00 | 0.8997 | 1.0081 | LN 197
314155 3CANBR T 115.00 | 0.9114 | 1.0086 | LN 2011
314156 3BRISTER 115.00 | 0.921 | 0.9995 | 6BRISTER-3BRISTER
314158 3GODW197 115.00 | 0.9115 | 1.0079 | LN 2011
314167 3OX 115.00 | 0.9206 | 0.9981 | 6OX-3OX
314176 6HARMONY 230.00 | 1.0704 | 1.0647 | LN 176
314203 6MACKEYS 230.00 | 1.0524 | 1.0319 | LN 2020
314204 6WINFA_1 230.00 | 1.0637 | 1.0339 | LN 2020
314325 3PURDYSW 115.00 | 1.051 | 1.0012 | LN 238
314348 2GRETN_1 69.000 | 1.0658 | 1.0227 | LN 173
314516 3BRUNS_1 115.00 | 1.0517 | 1.0197 | LN 238
314562 3CLUBHSE 115.00 | 1.0551 | 1.0055 | LN 238
314565 3CLBHS71 115.00 | 1.0551 | 1.0055 | LN 238
314570 3METCATP 115.00 | 1.053 | 1.0084 | LN 238
314572 3EMPORIA 115.00 | 1.0529 | 1.0088 | LN 238
314588 3METCALF 115.00 | 1.0514 | 1.0068 | LN 238
314637 6EDENTON 230.00 | 1.0563 | 1.0318 | LN 2020
314651 6WINFALL 230.00 | 1.0616 | 1.0319 | LN 2020
314662 6S HERTFORD 230.00 | 1.0602 | 1.0317 | LN 2020
314676 3BRUNSWK 115.00 | 1.0512 | 1.0192 | LN 238
314693 3FRMAN D 115.00 | 1.0538 | 1.0109 | LN 238
314704 3LAWRENC 115.00 | 1.0528 | 1.0169 | LN 238
314731 2GRETNA 69.000 | 1.0655 | 1.0225 | LN 173
314732 2GRNA FB 69.000 | 1.0655 | 1.0225 | LN 173
314735 2ALTAVISTADP69.000 | 1.0502 | 1.0296 | LN 173
314737 2SW35T57 69.000 | 1.0578 | 1.0254 | LN 173
314738 2MT AIRY 69.000 | 1.0565 | 1.024 | LN 173
314739 2MT A TP 69.000 | 1.0578 | 1.0254 | LN 173
314786 2GASBURG 69.000 | 1.0683 | 1.0352 | LN 238
314841 4CLFTN F 138.00 | 1.0699 | 1.0492 | LN 133
314850 3CLBHS_1 115.00 | 1.0556 | 1.006 | LN 238
314857 4LOWMOOR 138.00 | 1.0512 | 1.0451 | LN 112
314863 3EMPOR_1 115.00 | 1.0536 | 1.0094 | LN 238
314894 4LOWMO_1 138.00 | 1.0518 | 1.0456 | LN 112
341647 2HORSE CV KU69.000 | 0.9153 | 0.9693 | 5BARREN CO-5SUMM SHADE
341650 2HORSECAVE T69.000 | 0.9193 | 0.9732 | 5BARREN CO-5SUMM SHADE
341651 2HORSECAVE J69.000 | 0.9193 | 0.9732 | 5BARREN CO-5SUMM SHADE
901080 W1-029 230.00 | 1.0547 | 1.0296 | LN 2020
910571 X3-008 C 69.000 | 1.0758 | 1.072 | CKT 6702
910572 X3-008 E 69.000 | 1.0758 | 1.072 | CKT 6702
910590 X3-015 TAP 69.000 | 1.0713 | 1.0681 | VIENNA AT2
910591 X3-015 C 69.000 | 1.0713 | 1.0681 | VIENNA AT1
910592 X3-015 E 69.000 | 1.0713 | 1.0681 | VIENNA AT2
912052 X4-006 E 230.00 | 1.0578 | 1.0457 | V3_017_TAP86-V3-017
914031 Y2-015 C 230.00 | 1.0536 | 1.0426 | PL100142
914032 Y2-015 E 230.00 | 1.0536 | 1.0426 | PL100142
916040 Z1-036 TAP 230.00 | 1.0583 | 1.0318 | LN 2020
916041 Z1-036 C 230.00 | 1.0583 | 1.0318 | LN 2020
916042 Z1-036 E 230.00 | 1.0583 | 1.0318 | LN 2020

## SPP_N-1_VOLTAGE_SUM
BUS | VCONT pu | VINIT pu | CONTINGENCY
509240 CROCKET4 138.00 | 0.9306 | 1.0143 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509320 ALTO 4 138.00 | 0.9419 | 1.0029 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509321 BEREA 4 138.00 | 0.9302 | 1.0139 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509322 GRAPLND4 138.00 | 0.9321 | 1.0102 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509323 LATEXO 4 138.00 | 0.9309 | 1.0132 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509325 MUSTPR4 138.00 | 0.93 | 1.0125 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509326 SLOCUM 4 138.00 | 0.9339 | 1.0075 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
515193 COLBRT-4 138.00 | 0.9468 | 0.9733 | OPEN LINE FROM BUS 514809 [JOHNCO 7 345.00] TO BUS 514808 [JOHNCO 4 138.00] TO BUS 514810 [JOHNCO11 13.800] CKT 1
515544 RENFROW4 138.00 | 0.9471 | 1.0094 | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 1
515546 GRANTCO4 138.00 | 0.941 | 1.0012 | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 1
515554 BVRCNTY7 345.00 | 1.0647 | 1.0499 | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1
515569 MDFRDTP4 138.00 | 0.9483 | 1.008 | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 1
520409 SAND RDG_138138.00 | 0.9476 | 1.0084 | OPEN LINE FROM BUS 515543 [RENFROW7 345.00] TO BUS 515544 [RENFROW4 138.00] TO BUS 515545 [RENFRO11 13.800] CKT 1
520860 COLBERT4 138.00 | 0.9465 | 0.973 | OPEN LINE FROM BUS 514809 [JOHNCO 7 345.00] TO BUS 514808 [JOHNCO 4 138.00] TO BUS 514810 [JOHNCO11 13.800] CKT 1
520963 KIERSEY4 138.00 | 0.9486 | 0.9749 | OPEN LINE FROM BUS 514809 [JOHNCO 7 345.00] TO BUS 514808 [JOHNCO 4 138.00] TO BUS 514810 [JOHNCO11 13.800] CKT 1
522800 MU-TULIA 3115.00 | 0.932 | 0.9822 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
522888 LP-WADSWRTH6230.00 | 0.8876 | 0.9744 | OPEN LINE FROM BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1
523012 TC-ANTHY_TP3115.00 | 0.9257 | 1.02 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523024 TC-BEAVER 3115.00 | 0.9215 | 1.0162 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523097 HITCHLAND 7345.00 | 1.065 | 1.047 | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1
523099 TC-WHITING 3115.00 | 0.9449 | 0.9758 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523120 COLE 3115.00 | 0.9341 | 1.0273 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523135 LISPCOMB 3115.00 | 0.9232 | 1.0293 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523140 TXFARMS 3115.00 | 0.9355 | 1.0247 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523147 WADE 3115.00 | 0.9259 | 1.0316 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523154 OCHILTREE 3115.00 | 0.9292 | 1.0345 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523158 PERRYTON 3115.00 | 0.9287 | 1.0341 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1
523216 RB-HOGUE 3115.00 | 0.9465 | 1.0076 | OPEN LINE FROM BUS 523869 [CHAN/TASCOS6230.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1
523220 XIT_INTG 3115.00 | 0.9147 | 1.0142 | OPEN LINE FROM BUS 523869 [CHAN/TASCOS6230.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1
523221 XIT_INTG 6230.00 | 0.887 | 0.9881 | OPEN LINE FROM BUS 523869 [CHAN/TASCOS6230.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1
523228 DALLAM 3115.00 | 0.9329 | 1.0049 | OPEN LINE FROM BUS 523869 [CHAN/TASCOS6230.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1
523237 HILMARCHZ 3115.00 | 0.9336 | 1.0046 | OPEN LINE FROM BUS 523869 [CHAN/TASCOS6230.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1
523246 DALHART 3115.00 | 0.9325 | 1.0041 | OPEN LINE FROM BUS 523869 [CHAN/TASCOS6230.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1
523551 HUTCHISON 6230.00 | 0.9474 | 0.9775 | OPEN LINE FROM BUS 523551 [HUTCHISON 6230.00] TO BUS 524044 [NICHOLS 6230.00] CKT 1
523853 FINNEY 7345.00 | 1.09 | 1.0321 | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1
523869 CHAN/TASCOS6230.00 | 0.8844 | 0.9934 | OPEN LINE FROM BUS 523869 [CHAN/TASCOS6230.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1
523961 POTTER_CO 7345.00 | 1.0546 | 1.0246 | OPEN LINE FROM BUS 523959 [POTTER_CO 6230.00] TO BUS 523961 [POTTER_CO 7345.00] TO BUS 523957 [POTTER_TR 113.200] CKT 1
524163 EAST_PLANT 6230.00 | 0.9032 | 0.9848 | OPEN LINE FROM BUS 523977 [HARRNG_WST 6230.00] TO BUS 524163 [EAST_PLANT 6230.00] CKT 1
524296 SPNSPUR_WND7345.00 | 1.0571 | 1.027 | OPEN LINE FROM BUS 523959 [POTTER_CO 6230.00] TO BUS 523961 [POTTER_CO 7345.00] TO BUS 523957 [POTTER_TR 113.200] CKT 1
524694 DS-#22 3115.00 | 0.9396 | 0.9519 | OPEN LINE FROM BUS 524623 [DEAFSMITH 6230.00] TO BUS 524622 [DEAFSMITH 3115.00] TO BUS 524620 [DEFSMTH_TR1113.200] CKT 1
524885 SN_JUAN_TAP6230.00 | 0.9046 | 0.9905 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
524889 SN_JUAN_WND6230.00 | 0.9044 | 0.9904 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
525018 EMULESH&VLY3115.00 | 0.9409 | 0.966 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525019 EMU&VLY_TP 3115.00 | 0.9412 | 0.9662 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525028 BAILEYCO 3115.00 | 0.9362 | 0.9637 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525040 BAILEY_PMP 3115.00 | 0.9322 | 0.9751 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525154 HAPPY_INT 3115.00 | 0.9349 | 0.9782 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525179 TULIA_TP 3115.00 | 0.9333 | 0.9835 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525192 KRESS_INT 3115.00 | 0.9335 | 0.9933 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525212 SWISHER 3115.00 | 0.9336 | 1.006 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525225 KRESS_RURAL3115.00 | 0.9332 | 0.9862 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525257 N_PLAINVEW 3115.00 | 0.9341 | 0.9781 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525272 KISER 3115.00 | 0.9346 | 0.9774 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525326 COX 3115.00 | 0.939 | 0.9739 | OPEN LINE FROM BUS 525213 [SWISHER 6230.00] TO BUS 525212 [SWISHER 3115.00] TO BUS 525211 [SWISHER_TR1113.200] CKT 1
525549 TOLK 7345.00 | 1.0858 | 1.014 | OPEN LINE FROM BUS 525543 [TOLK_TAP 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1
525594 SUDANRURAL 3115.00 | 0.9291 | 0.9841 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525608 NEW_AMHERST3115.00 | 0.9265 | 0.9927 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525614 W_LITLFLDTP3115.00 | 0.9471 | 1.0099 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525615 W_LITTLFLD 3115.00 | 0.9471 | 1.0099 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525636 LAMB_CNTY 3115.00 | 0.9301 | 1.014 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
525637 LAMB_CNTY 6230.00 | 0.8369 | 0.9506 | OPEN LINE FROM BUS 525531 [TOLK_WEST 6230.00] TO BUS 525637 [LAMB_CNTY 6230.00] CKT 1
526299 LUBBCK_EST 6230.00 | 0.8874 | 0.9751 | OPEN LINE FROM BUS 526299 [LUBBCK_EST 6230.00] TO BUS 526337 [JONES 6230.00] CKT 1
526435 SUNDOWN 6230.00 | 0.9467 | 0.9713 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
526460 AMOCO_SS 6230.00 | 0.9422 | 0.9714 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
526656 LYNN_CNTY 3115.00 | 0.9006 | 0.9765 | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1
526676 GRASSLAND 3115.00 | 0.8914 | 0.9819 | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1
526677 GRASSLAND 6230.00 | 0.9015 | 0.9878 | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1
526679 CIRRUS_WND 6230.00 | 0.9017 | 0.9881 | OPEN LINE FROM BUS 526337 [JONES 6230.00] TO BUS 526677 [GRASSLAND 6230.00] CKT 1
526694 GRAHAM 3115.00 | 0.8699 | 0.9653 | OPEN LINE FROM BUS 526677 [GRASSLAND 6230.00] TO BUS 526676 [GRASSLAND 3115.00] TO BUS 526674 [GRASLND_TR1113.200] CKT 1
526784 AMOCOWASSON6230.00 | 0.944 | 0.9932 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
526935 YOAKUM 6230.00 | 0.9294 | 0.9911 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
526936 YOAKUM_345 345.00 | 0.9184 | 1.0066 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527010 OXYBRU_TP 6230.00 | 0.936 | 0.992 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527018 BENNETT 3115.00 | 0.9329 | 1.0031 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527021 CORTEZ 3115.00 | 0.8883 | 0.9866 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527022 APACHE_ROB 3115.00 | 0.8884 | 0.9866 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527024 ALLRED_SUB 3115.00 | 0.889 | 0.9871 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527030 ALRDCRTZ_TP3115.00 | 0.8902 | 0.9883 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527036 SHELL_C2 3115.00 | 0.9131 | 0.9972 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527041 ARCO_TP 3115.00 | 0.9333 | 1.0034 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527046 ARCO_WILRD 3115.00 | 0.9313 | 1.0015 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527047 OXY_WILRD 3115.00 | 0.9313 | 1.0016 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527051 ODC_TP 3115.00 | 0.9329 | 1.0031 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527056 ODC 3115.00 | 0.9311 | 1.0015 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527062 SHELL_CO2 3115.00 | 0.931 | 1.0022 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527068 SHELLC3_TP 3115.00 | 0.9039 | 0.9935 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527074 SHELLC3 3115.00 | 0.9037 | 0.9934 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527080 EL_PASO 3115.00 | 0.9301 | 1.002 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527105 SAN_ANDS_TP3115.00 | 0.9272 | 1.0038 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527106 SAN_ANDRES 3115.00 | 0.9253 | 1.002 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527130 DENVER_N 3115.00 | 0.9283 | 1.0038 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527136 DENVER_S 3115.00 | 0.9283 | 1.0038 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527146 MUSTANG 3115.00 | 0.9398 | 1.0072 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527194 LG-PLSHILL 3115.00 | 0.9381 | 1.0045 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527202 SEAGRAVES 3115.00 | 0.9336 | 1.0003 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527212 DIAMONDBACK3115.00 | 0.9291 | 0.9933 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527238 ROZ 3115.00 | 0.929 | 1.0164 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527242 AMERADA 3115.00 | 0.9289 | 1.0163 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527262 SULPHUR 3115.00 | 0.9325 | 0.9954 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527275 SEMINOLE 3115.00 | 0.9304 | 1.0174 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527276 SEMINOLE 6230.00 | 0.8871 | 0.9742 | OPEN LINE FROM BUS 527149 [MUSTANG 6230.00] TO BUS 527276 [SEMINOLE 6230.00] CKT 1
527284 RUSSELL 3115.00 | 0.868 | 0.9937 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527286 XTO_RUSSEL 3115.00 | 0.8723 | 0.9944 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527300 AM_FRAC 3115.00 | 0.8472 | 0.9883 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527322 GAINES 3115.00 | 0.8907 | 1.0002 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527323 OXY_WSTSEM 3115.00 | 0.8862 | 0.9977 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527325 OXY_WSEM_TP3115.00 | 0.8879 | 0.9992 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527340 DOSS 3115.00 | 0.9089 | 1.0069 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527346 LEGACY 3115.00 | 0.8953 | 1.0006 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527360 MAPCO 3115.00 | 0.8474 | 0.9884 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527362 JOHNSON_DRW3115.00 | 0.8476 | 0.9887 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527363 HIGG 3115.00 | 0.8688 | 0.9944 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527482 CHAVES_CNTY3115.00 | 0.8353 | 0.9891 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527483 CHAVES_CNTY6230.00 | 0.854 | 0.9968 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527501 URTON 3115.00 | 0.8228 | 0.9802 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527508 PRICE 3115.00 | 0.8219 | 0.9791 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527515 CV-PINE 3115.00 | 0.8177 | 0.9762 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527522 ROSWELL_CTY3115.00 | 0.8147 | 0.9748 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527534 BRASHER_TP 3115.00 | 0.8109 | 0.9733 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527536 BRASHER 3115.00 | 0.8094 | 0.972 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527541 CAPITAN 3115.00 | 0.8127 | 0.9732 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527546 SAMSON 3115.00 | 0.8164 | 0.9767 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527564 ROSWLL_INT 3115.00 | 0.8109 | 0.9734 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527597 TWEEDY 3115.00 | 0.8095 | 0.973 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527707 ARTESIA 3115.00 | 0.7889 | 0.9814 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527711 EAGLE_CREEK3115.00 | 0.7901 | 0.9818 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527715 NAVAJO_2TP 3115.00 | 0.7893 | 0.9811 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527717 NAVAJO_2 3115.00 | 0.7892 | 0.9811 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527720 NAVAJO_3 3115.00 | 0.7892 | 0.9811 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527736 NAVAJO_5TP 3115.00 | 0.7889 | 0.9809 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527739 NAVAJO_4 3115.00 | 0.7889 | 0.9808 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527743 NAVAJO_5 3115.00 | 0.7889 | 0.9808 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527786 ATOKA 3115.00 | 0.7949 | 0.986 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527793 EDDY_STH 3115.00 | 0.8194 | 0.9944 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527798 EDDY_NTH 3115.00 | 0.8194 | 0.9944 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527799 EDDY_NORTH 6230.00 | 0.8498 | 1 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527800 EDDY_SOUTH 6230.00 | 0.8498 | 1 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527802 EDDY_CNTY 7345.00 | 0.8782 | 1.0046 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527821 CV-DAYTON 3115.00 | 0.7963 | 0.9863 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527828 CV-12MH 3115.00 | 0.8178 | 0.993 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527864 CUNNINHAM 3115.00 | 0.8278 | 1.0148 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527865 CUNNINHAM 6230.00 | 0.8634 | 1.0145 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527891 HOBBS_INT 3115.00 | 0.8426 | 1.02 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527894 HOBBS_INT 6230.00 | 0.8608 | 1.0153 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527896 HOBBS_INT 7345.00 | 0.8599 | 1.0106 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527930 PCA 3115.00 | 0.7581 | 1.0044 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527953 LIVSTNRIDGE3115.00 | 0.5299 | 0.9855 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527955 SAGE_BRUSH 3115.00 | 0.5463 | 0.9786 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527957 LAGARTO 3115.00 | 0.5701 | 0.9833 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527962 POTASH_JCT 3115.00 | 0.7689 | 1.0207 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527963 POTASH_JCT 6230.00 | 0.7908 | 0.9787 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527965 KIOWA 7345.00 | 0.8008 | 1.0058 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527999 INTREPDW_TP3115.00 | 0.742 | 1.0154 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528000 INTREPIDWST3115.00 | 0.7409 | 1.0146 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528009 WIPP 3115.00 | 0.5026 | 0.9887 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528016 SAND_DUNES 3115.00 | 0.4499 | 0.9903 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528018 RED_BLUFF 3115.00 | 0.398 | 1 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528020 BOPCO_PKRLK3115.00 | 0.4359 | 0.9916 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528025 RDRUNNER 3115.00 | 0.3652 | 1.0044 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528027 RDRUNNER 7345.00 | 0.332 | 0.9727 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528035 IMC_#1_TP 3115.00 | 0.6701 | 1.0035 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528037 IMC_#1 3115.00 | 0.669 | 1.0027 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528040 BATTLE_AXE 3115.00 | 0.3426 | 0.9911 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528070 CV-AZMESA 3115.00 | 0.8034 | 1.0082 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528076 CV-WALTCYN 3115.00 | 0.8013 | 1.0068 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528079 CV-CONEBUTE3115.00 | 0.8011 | 1.0067 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528094 7-RIVERS 3115.00 | 0.8159 | 1.0143 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528095 7-RIVERS 6230.00 | 0.8099 | 0.9844 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528109 CV-LAKEWOOD3115.00 | 0.8036 | 0.9988 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528116 CV-IRISHHIL3115.00 | 0.7998 | 0.9933 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528132 OCOTILLO 3115.00 | 0.766 | 0.9876 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528137 N_CANAL 3115.00 | 0.7711 | 0.9915 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528151 FIESTA 3115.00 | 0.7692 | 0.9943 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528160 CARLSBAD 3115.00 | 0.7703 | 0.9952 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528178 PECOS 3115.00 | 0.7748 | 0.9944 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528179 PECOS 6230.00 | 0.7937 | 0.9822 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528182 NORTH_LOVNG3115.00 | 0.7816 | 1.0256 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528185 NLOV_PLT 7345.00 | 0.8028 | 1.0254 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528192 SOUTH_LOVNG3115.00 | 0.7777 | 1.0226 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528222 CHINA_DRAW 3115.00 | 0.7082 | 1.0266 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528223 CHINA_DRAW 7345.00 | 0.7774 | 1.0186 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528226 HOPI_SUB 3115.00 | 0.7719 | 1.0042 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528228 WOOD_DRAW 3115.00 | 0.48 | 0.9896 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528230 AGAVE_RHILL3115.00 | 0.3612 | 0.9687 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528232 OCHOA 3115.00 | 0.3619 | 0.968 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528239 PNDEROSATP 3115.00 | 0.4207 | 0.9631 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528240 PONDEROSA 3115.00 | 0.4122 | 0.9578 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528246 YESO_HILLS 3115.00 | 0.6831 | 1.0107 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528317 ENRON_TP 3115.00 | 0.766 | 0.9907 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528318 ENRON 3115.00 | 0.7656 | 0.9904 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528325 LE-WAITS 3115.00 | 0.8622 | 0.9833 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528334 LE-LOVINTON3115.00 | 0.8339 | 0.9864 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528341 LE-SANANDRS3115.00 | 0.8003 | 0.9942 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528348 BUCKEYE_TP 3115.00 | 0.808 | 1 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528355 MADDOX 3115.00 | 0.8341 | 1.0186 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528385 BUCKEYE 3115.00 | 0.8077 | 0.9998 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528392 PEARLE 3115.00 | 0.7839 | 0.9911 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528394 QUAHADA 3115.00 | 0.766 | 0.9934 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528399 LEA_NATIONL3115.00 | 0.7659 | 0.9907 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528406 MALJMAR1&2 3115.00 | 0.7446 | 0.9773 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528413 TAYLOR 3115.00 | 0.8176 | 0.9967 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528420 ZIA 3115.00 | 0.7627 | 0.991 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528435 MILLEN 3115.00 | 0.8172 | 0.9975 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528442 NE_HOBBS 3115.00 | 0.8157 | 0.9958 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528449 W_BENDER 3115.00 | 0.8186 | 1.0024 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528456 N_HOBBS 3115.00 | 0.8099 | 0.9953 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528463 SANGER_SW 3115.00 | 0.8216 | 1.0057 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528470 E_SANGER 3115.00 | 0.8135 | 0.9965 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528477 S_HOBBS 3115.00 | 0.8038 | 1.0012 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528480 OXY_S_HOBBS3115.00 | 0.8036 | 1.0067 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528484 SW_4J44 3115.00 | 0.8038 | 1.0078 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528491 MONUMENT 3115.00 | 0.8241 | 1.0161 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528498 W_HOBBS 3115.00 | 0.8044 | 1.0104 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528505 LEA_ROAD 3115.00 | 0.6019 | 0.9704 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528505 LEA_ROAD 3115.00 | 0.9188 | 0.9704 | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 528604 [ANDREWS 6230.00] CKT 1
528512 EUNICE 3115.00 | 0.7737 | 1.0329 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528519 WARD 3115.00 | 0.5438 | 0.9676 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528526 TEAGUE 3115.00 | 0.5978 | 0.9955 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528533 DRINKARD_TP3115.00 | 0.7745 | 1.0323 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528540 WHITTEN 3115.00 | 0.4794 | 0.9669 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528547 S_JAL 3115.00 | 0.5181 | 0.9733 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528552 OIL_CENTER 3115.00 | 0.6408 | 0.9765 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528554 COOPER_RNCH3115.00 | 0.6657 | 0.9806 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528561 DOLLARHIDE 3115.00 | 0.5053 | 0.9649 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528564 TOBOSOFLATS3115.00 | 0.497 | 0.9598 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528568 MONUMNT_TP 3115.00 | 0.7573 | 0.9994 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528575 OXYPERMIAN 3115.00 | 0.8197 | 1.0037 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528582 BYRD 3115.00 | 0.715 | 0.9898 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528589 DRINKARD 3115.00 | 0.7703 | 1.0356 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528596 CARDINAL 3115.00 | 0.6556 | 1.0121 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528603 NA_ENRICH 3115.00 | 0.7576 | 1.0449 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528604 ANDREWS 6230.00 | 0.7712 | 0.9797 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528605 TARGA 3115.00 | 0.6955 | 1.0244 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528775 LE-ERF 3115.00 | 0.8476 | 0.9887 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528792 LE-TEXACO 3115.00 | 0.8038 | 0.9968 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
530554 ATWOOD 3 115.00 | 0.7789 | 0.9844 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530555 COLBY 3 115.00 | 0.7797 | 1.0161 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530556 HOXIE 3 115.00 | 0.7935 | 0.9852 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530557 BEACH 3 115.00 | 0.847 | 0.9817 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530559 PH RUN 3 115.00 | 0.7904 | 0.9998 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530605 REDLIN 3 115.00 | 0.9013 | 0.9944 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530606 ALXNDR 3 115.00 | 0.9287 | 0.99 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530607 NESCTY 3 115.00 | 0.8927 | 0.9844 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530608 NEKOMA 3 115.00 | 0.9434 | 0.9928 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530623 RICE 3 115.00 | 0.9424 | 1.0196 | OPEN LINE FROM BUS 530686 [RICE 6 230.00] TO BUS 530623 [RICE 3 115.00] TO BUS 530687 [RICET1 12.470] CKT 1
530681 BUSHTON3 115.00 | 0.9424 | 1.0156 | OPEN LINE FROM BUS 530686 [RICE 6 230.00] TO BUS 530623 [RICE 3 115.00] TO BUS 530687 [RICET1 12.470] CKT 1
530682 SEGNTP 3 115.00 | 0.7902 | 0.9965 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530683 SEGUIN 3 115.00 | 0.79 | 0.9972 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530686 RICE 6 230.00 | 0.935 | 0.9988 | OPEN LINE FROM BUS 530686 [RICE 6 230.00] TO BUS 532871 [CIRCLE 6 230.00] CKT 1
530688 BUFLOCRK6 230.00 | 0.9387 | 1.0026 | OPEN LINE FROM BUS 530686 [RICE 6 230.00] TO BUS 532871 [CIRCLE 6 230.00] CKT 1
531220 HERNTAP3 115.00 | 0.7835 | 0.9798 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531351 BREWSTR3 115.00 | 0.7848 | 1.0167 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531352 CHASE 3 115.00 | 0.865 | 0.9987 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531353 GOODLND3 115.00 | 0.7862 | 1.0106 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531354 KANARAD3 115.00 | 0.814 | 1.0061 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531355 NSI 115.00 | 0.8043 | 1.0077 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531356 NSI TAP3 115.00 | 0.8047 | 1.008 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531357 RULETON3 115.00 | 0.7964 | 1.01 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531358 SHARNSP3 115.00 | 0.865 | 0.9988 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531359 BEELER 3 115.00 | 0.9082 | 0.9857 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531360 DIGHTNT3 115.00 | 0.9466 | 0.9977 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531361 DIGHTON3 115.00 | 0.9459 | 0.9971 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531362 MANNGT 3 115.00 | 0.9444 | 1.0034 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531363 MANNING3 115.00 | 0.9418 | 1.001 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531364 ATWODSW3 115.00 | 0.7821 | 0.981 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531365 BIRDCTY3 115.00 | 0.7798 | 0.9921 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531366 CNORTON3 115.00 | 0.8465 | 0.9802 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531367 HERNDON3 115.00 | 0.791 | 0.9782 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531368 LAWNRID3 115.00 | 0.7865 | 1.0015 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531369 NATWOOD3 115.00 | 0.782 | 0.9809 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531370 STFRAN 3 115.00 | 0.781 | 0.9951 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531371 JOHNSON3 115.00 | 0.801 | 0.9764 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531372 NORCATR3 115.00 | 0.8223 | 0.9772 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531373 RHOADES3 115.00 | 0.8465 | 0.9802 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531386 GRHMSUB3 115.00 | 0.8444 | 0.9793 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531409 ARNOLD3 115.00 | 0.8527 | 0.9853 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531411 GOVE 3 115.00 | 0.8155 | 0.9916 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531412 GRINNEL3 115.00 | 0.7962 | 0.9966 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531414 RANSOM 3 115.00 | 0.8613 | 0.9847 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531416 CTYSERT3 115.00 | 0.9475 | 1.0186 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531418 CTYSERV3 115.00 | 0.9475 | 1.0186 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531428 LEOTI 3 115.00 | 0.9482 | 1.0032 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531429 MINGO 3 115.00 | 0.7876 | 1.0338 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531431 PALMER3 115.00 | 0.9115 | 1.0001 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531433 SCOTCTY3 115.00 | 0.9472 | 1.0122 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531434 SELKIRK3 115.00 | 0.9458 | 1.0022 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531438 TRIB SW3 115.00 | 0.9274 | 1.0011 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531439 TRIBUNE3 115.00 | 0.9285 | 1.0008 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531441 CSTFRAN3 115.00 | 0.7815 | 0.9959 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531443 GODLNDT3 115.00 | 0.7863 | 1.0103 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531444 GOODCTY3 115.00 | 0.7811 | 1.0063 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531456 NESSCTY3 115.00 | 0.8927 | 0.9844 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531457 OBER T 3 115.00 | 0.8034 | 0.9763 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531458 OBERLIN3 115.00 | 0.8031 | 0.9761 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531464 SETAB 3 115.00 | 0.9476 | 1.0192 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531471 STFRANT3 115.00 | 0.7817 | 0.996 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531485 CNTRLPL3 115.00 | 0.948 | 1.0109 | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1
531487 MCDONLD3 115.00 | 0.7779 | 0.9875 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531488 BVERVLLY 115.00 | 0.7781 | 0.987 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531489 ONEOK 3 115.00 | 0.7779 | 0.9868 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
532769 LANG 7 345.00 | 0.9236 | 1.0174 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
533301 EAST ST3 115.00 | 0.9445 | 1.0251 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
533302 EEUREKA3 115.00 | 0.9279 | 1.0013 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
533304 LANG 3 115.00 | 0.9473 | 1.0323 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
533307 PRAIRIE3 115.00 | 0.9481 | 1.0243 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
533308 VAUGHN 3 115.00 | 0.9377 | 1.0102 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
539662 ELLSWTH3 115.00 | 0.9444 | 1.0071 | OPEN LINE FROM BUS 530686 [RICE 6 230.00] TO BUS 530623 [RICE 3 115.00] TO BUS 530687 [RICET1 12.470] CKT 1
541197 MULLNCR7 345.00 | 1.0526 | 1.0384 | OPEN LINE FROM BUS 541197 [MULLNCR7 345.00] TO BUS 541357 [MULLNCR2 69.000] TO BUS 541373 [MULLNCR1 13.800] CKT 1
640214 HASTING4 230.00 | 0.9096 | 0.9538 | OPEN LINE FROM BUS 640200 [GR ISLD4 230.00] TO BUS 640214 [HASTING4 230.00] CKT 1
640325 REDWILO3 345.00 | 1.0578 | 1.0417 | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1
640330 RIVERDL4 230.00 | 0.9347 | 0.9543 | OPEN LINE FROM BUS 640200 [GR ISLD4 230.00] TO BUS 640330 [RIVERDL4 230.00] CKT 1
645740 S3740 3 345.00 | 1.0594 | 1.0395 | OPEN LINE FROM BUS 645455 [S3455 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1
648506 PR BRZ 4 230.00 | 1.0572 | 1.0502 | OPEN LINE FROM BUS 640226 [HOSKINS3 345.00] TO BUS 635200 [RAUN 3 345.00] CKT 1

## SERC_N-1_VOLTAGE_SUM
BUS | VCONT | VINIT | CONTINGENCY
300074 5CUBA3 161.00 | 0.9386 | 0.9695 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300077 5FLETCH 161.00 | 0.9457 | 0.9968 | OPEN LINE FROM BUS 300040 [7FLETCH 345.00] TO BUS 300077 [5FLETCH 161.00] TO BUS 300175 [1FLTCHTR 13.800] CKT 1
300094 5LOCUST 161.00 | 0.9431 | 0.9624 | OPEN LINE FROM BUS 300039 [7FAIRPT 345.00] TO BUS 300076 [5FAIRPT 161.00] CKT 3
300112 5SALEM 161.00 | 0.9487 | 0.9978 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300119 5SULLVN 161.00 | 0.941 | 0.965 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300142 4SULVN 138.00 | 0.9408 | 0.9634 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300858 5SMRSVLEST 161.00 | 0.948 | 0.9718 | OPEN LINE FROM BUS 300040 [7FLETCH 345.00] TO BUS 300077 [5FLETCH 161.00] TO BUS 300175 [1FLTCHTR 13.800] CKT 1
301136 5BOURBN 161.00 | 0.9402 | 0.9661 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
301144 4PRIDGE 138.00 | 0.9478 | 0.9657 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
301149 5STEELV 161.00 | 0.941 | 0.9783 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
304400 8RICH REACTO500.00 | 1.0923 | 1.043 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
305098 3E10-ROCKFIS115.00 | 0.9357 | 0.9481 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304391 [8CUMBLND500T500.00] CKT 1
306002 BLREC30 100.00 | 1.0586 | 1.0575 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306008 8OCONEE 500.00 | 1.0812 | 1.0751 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 380011 [8S HALL 500.00] CKT 1
306009 ANDERSON 100.00 | 1.0621 | 1.0609 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306010 IND 306010 100.00 | 1.0609 | 1.06 | OPEN LINE FROM BUS 380011 [8S HALL 500.00] TO BUS 382035 [6S HALL LS 230.00] CKT 1
306011 IND 306011 100.00 | 1.055 | 1.0538 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306012 IND 306012 100.00 | 1.0565 | 1.0553 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306017 CENTRAL 100.00 | 1.0622 | 1.0613 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306025 IND 306025 100.00 | 1.0609 | 1.0597 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306027 BUS 306027 100.00 | 1.062 | 1.0608 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306031 BUS 306031 100.00 | 1.0572 | 1.056 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306032 BUS 306032 100.00 | 1.0553 | 1.0541 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306048 IND 306048 100.00 | 1.0618 | 1.0606 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306049 IND 306049 100.00 | 1.0619 | 1.0607 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306050 IND 306050 100.00 | 1.0617 | 1.0605 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306051 IND 306051 100.00 | 1.0619 | 1.0607 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306065 SUMMEY R 100.00 | 1.0586 | 1.0577 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306067 IND 306067 100.00 | 1.0559 | 1.0547 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306068 BUS 306068 100.00 | 1.0559 | 1.0547 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306070 BUS 306070 100.00 | 1.056 | 1.0548 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306112 8BAD CRK 500.00 | 1.0905 | 1.0862 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309002 [8KATRTRT 500.00] CKT Z1
306113 8JOCASSE 500.00 | 1.0885 | 1.0832 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309002 [8KATRTRT 500.00] CKT Z1
306114 AHLSTROM 100.00 | 1.053 | 1.0517 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306115 BUS 306115 100.00 | 1.0532 | 1.052 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306116 BUS 306116 100.00 | 1.0532 | 1.052 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306119 IND 306119 100.00 | 1.0526 | 1.0514 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306140 EASLY 4T 100.00 | 1.0536 | 1.0524 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306154 GREENLWN 100.00 | 1.0538 | 1.0525 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306197 IND 306197 100.00 | 1.0559 | 1.0547 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306237 ALEXNDRT 100.00 | 1.054 | 1.0526 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306245 CLIFSID 100.00 | 1.0597 | 1.0586 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306253 FAIRVIEW 100.00 | 1.0533 | 1.0517 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306285 OAKLND T 100.00 | 1.0531 | 1.0516 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306288 IND 306288 100.00 | 1.0569 | 1.0557 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306289 IND 306289 100.00 | 1.0533 | 1.0521 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
306291 PINKTPFV 100.00 | 1.057 | 1.0558 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306293 PNK HARL 100.00 | 1.0531 | 1.0518 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306295 SCHNEIDR 100.00 | 1.0526 | 1.0526 | BASE CASE
306337 8NEWPORT 500.00 | 1.0772 | 1.0649 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
306340 IND 306340 100.00 | 1.056 | 1.055 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306362 ELLIOT R 100.00 | 1.0531 | 1.0521 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306389 BUS 306389 100.00 | 1.0537 | 1.0527 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306401 SHELBY 100.00 | 1.053 | 1.052 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306416 WATEREE 100.00 | 1.0709 | 1.0688 | OPEN LINE FROM BUS 312706 [6BLYTHE 230.00] TO BUS 312715 [6LUGOFF 230.00] CKT 1
306546 8MCGUIRE 500.00 | 1.0788 | 1.0758 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306712 6ANTIOCH 230.00 | 1.052 | 1.0435 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309035 [8ROCKSPGRTRT500.00] CKT Z1
306719 8ANTIOCH 500.00 | 1.0873 | 1.0759 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309035 [8ROCKSPGRTRT500.00] CKT Z1
306737 DAN RIV 100.00 | 1.0562 | 1.0551 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
306761 MEADOWGR 100.00 | 1.0547 | 1.0536 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
306764 MOTLEY 100.00 | 1.0565 | 1.0555 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
306836 8WOODLF 500.00 | 1.0897 | 1.0729 | OPEN LINE FROM BUS 306850 [8PL GRDN 500.00] TO BUS 309057 [8GODBEYRTRT 500.00] CKT Z1
306849 8PARKWOD 500.00 | 1.0565 | 1.0449 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 306836 [8WOODLF 500.00] CKT 1
306850 8PL GRDN 500.00 | 1.065 | 1.0521 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 306836 [8WOODLF 500.00] CKT 1
307511 BUS 307511 100.00 | 1.0624 | 1.0615 | OPEN LINE FROM BUS 380011 [8S HALL 500.00] TO BUS 382035 [6S HALL LS 230.00] CKT 1
307524 BUS 307524 100.00 | 1.053 | 1.0521 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
307525 ROCHESTER 100.00 | 1.0534 | 1.0525 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
307538 WYNDPTRET 100.00 | 1.053 | 1.0521 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
307551 BUS 307551 100.00 | 1.0534 | 1.0525 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308602 DNRVRGEN 100.00 | 1.0566 | 1.0556 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
308704 LIBRET 100.00 | 1.0552 | 1.0541 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308708 BUS 308708 100.00 | 1.0624 | 1.0615 | OPEN LINE FROM BUS 380011 [8S HALL 500.00] TO BUS 382035 [6S HALL LS 230.00] CKT 1
308710 BUS 308710 100.00 | 1.0624 | 1.0615 | OPEN LINE FROM BUS 380011 [8S HALL 500.00] TO BUS 382035 [6S HALL LS 230.00] CKT 1
308723 SSPRGSTR 100.00 | 1.053 | 1.052 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308752 EASLY4BT 100.00 | 1.0538 | 1.0526 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308753 EASLYC4B 100.00 | 1.0521 | 1.0508 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308788 8CLFSDTAP 500.00 | 1.1181 | 1.097 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309160 [8S_MTNRTRT 500.00] CKT Z1
308790 ALEX DUM 100.00 | 1.0527 | 1.0513 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308793 CLIFS2 100.00 | 1.0585 | 1.0574 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308948 PINKTPCF B 100.00 | 1.055 | 1.0537 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308953 PINKTPCF 100.00 | 1.0523 | 1.0511 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308955 IND 308955 100.00 | 1.0544 | 1.0534 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
309001 8ASBRTRT 500.00 | 1.0971 | 1.0751 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309001 [8ASBRTRT 500.00] CKT Z1
309002 8KATRTRT 500.00 | 1.0895 | 1.0751 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309002 [8KATRTRT 500.00] CKT Z1
309003 8ASBRTR 500.00 | 1.0971 | 1.0751 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309001 [8ASBRTRT 500.00] CKT Z1
309004 ANDERCAP 100.00 | 1.0621 | 1.0609 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
309011 8KATRTR 500.00 | 1.0895 | 1.0751 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309002 [8KATRTRT 500.00] CKT Z1
309014 GRLAWCAP 100.00 | 1.0538 | 1.0525 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309021 FAIRVCAP 100.00 | 1.0533 | 1.0517 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309025 8RICHMNRTRT 500.00 | 1.0772 | 1.0649 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
309035 8ROCKSPGRTRT500.00 | 1.0758 | 1.0758 | BASE CASE
309057 8GODBEYRTRT 500.00 | 1.0525 | 1.0521 | OPEN LINE FROM BUS 306849 [8PARKWOD 500.00] TO BUS 306850 [8PL GRDN 500.00] CKT 1
309160 8S_MTNRTRT 500.00 | 1.1237 | 1.0758 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309160 [8S_MTNRTRT 500.00] CKT Z1
309161 8S_MTNRTR 500.00 | 1.1237 | 1.0758 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309160 [8S_MTNRTRT 500.00] CKT Z1
309162 8ROCKSPGRTR 500.00 | 1.094 | 1.0758 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309035 [8ROCKSPGRTRT500.00] CKT Z1
309163 8RICHMNRTR 500.00 | 1.0772 | 1.0649 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
309164 8GODBEYRTR 500.00 | 1.0961 | 1.0521 | OPEN LINE FROM BUS 306850 [8PL GRDN 500.00] TO BUS 309057 [8GODBEYRTRT 500.00] CKT Z1
309322 FAIRVIE2 100.00 | 1.0533 | 1.0517 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309326 PNK HAR2 100.00 | 1.0531 | 1.0518 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309360 DANRVR 100.00 | 1.0562 | 1.0551 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
309362 MOTLEY2 100.00 | 1.0565 | 1.0555 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
309501 CENT1 100.00 | 1.0622 | 1.0613 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309502 CENT2 100.00 | 1.0622 | 1.0613 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309503 CENT3 100.00 | 1.0622 | 1.0613 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309504 CENT4 100.00 | 1.0622 | 1.0613 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309541 SHE4 100.00 | 1.053 | 1.052 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309542 SHE2 100.00 | 1.053 | 1.052 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309543 SHE3 100.00 | 1.053 | 1.052 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309577 AND1 100.00 | 1.0621 | 1.0609 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
309578 AND2 100.00 | 1.0621 | 1.0609 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
309580 AND4 100.00 | 1.0621 | 1.0609 | OPEN LINE FROM BUS 306005 [6HODGES 230.00] TO BUS 309419 [1HODGE 2 1.0000] CKT 2
309581 CLIF1 100.00 | 1.0597 | 1.0586 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309582 CLIF2 100.00 | 1.0597 | 1.0586 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
324072 8PINEVL 500.00 | 1.0925 | 1.0598 | OPEN LINE FROM BUS 324073 [8POCKETN 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1
324073 8POCKETN 500.00 | 1.0925 | 1.0556 | OPEN LINE FROM BUS 324073 [8POCKETN 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1
324115 7W FRANK 345.00 | 0.934 | 1.0076 | OPEN LINE FROM BUS 324105 [7GHENT 345.00] TO BUS 324115 [7W FRANK 345.00] CKT 1
324203 4AMERICN 138.00 | 0.9413 | 0.9669 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324212 4BLUE LK 138.00 | 0.9346 | 1.0087 | OPEN LINE FROM BUS 324101 [7BLUE LK 345.00] TO BUS 324212 [4BLUE LK 138.00] CKT 1
324258 4HAEFLNG 138.00 | 0.9438 | 0.9727 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324264 4IBM N LC 138.00 | 0.9437 | 0.9713 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324269 4LANSDW 138.00 | 0.9434 | 0.9656 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324275 4LOUDON 138.00 | 0.9442 | 0.9684 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324285 4MUD LAN 138.00 | 0.9462 | 0.9904 | OPEN LINE FROM BUS 324101 [7BLUE LK 345.00] TO BUS 324212 [4BLUE LK 138.00] CKT 1
324301 4REYNOLD 138.00 | 0.9451 | 0.9683 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324312 4TOYT N 138.00 | 0.944 | 0.9646 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324313 4TOYT S 138.00 | 0.9444 | 0.9653 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324317 4VILEY 138.00 | 0.9449 | 0.9769 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
324335 4INNOVAT 138.00 | 0.9439 | 0.9718 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
326548 4IBM N 138.00 | 0.9437 | 0.9713 | OPEN LINE FROM BUS 324116 [7W LEXNG 345.00] TO BUS 324320 [4W LEXNG 138.00] CKT 1
360024 5FREEPORT TN161.00 | 1.0568 | 1.0495 | OPEN LINE FROM BUS 360024 [5FREEPORT TN161.00] TO BUS 360725 [5FREEPORT #2161.00] CKT Z1
360026 5CORDOVA #1 161.00 | 1.0562 | 1.0427 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
360049 5DAVIDSON #1161.00 | 1.0525 | 1.0387 | OPEN LINE FROM BUS 360049 [5DAVIDSON #1161.00] TO BUS 361749 [5DAVIDSONSVC161.00] CKT Z1
360058 8E POINT AL 500.00 | 1.0603 | 1.0538 | OPEN LINE FROM BUS 360058 [8E POINT AL 500.00] TO BUS 360059 [5E POINT AL 161.00] CKT 1
360065 8WID CRK FP 500.00 | 1.0588 | 1.054 | OPEN LINE FROM BUS 360079 [8RACCOON MTN500.00] TO BUS 360664 [5RACCOON MT2161.00] CKT 5
360078 5PLATEAU TN 161.00 | 1.0532 | 1.0423 | OPEN LINE FROM BUS 360078 [5PLATEAU TN 161.00] TO BUS 361417 [5CAMPBEL JCT161.00] CKT 1
360079 8RACCOON MTN500.00 | 1.0605 | 1.0496 | OPEN LINE FROM BUS 360079 [8RACCOON MTN500.00] TO BUS 360664 [5RACCOON MT2161.00] CKT 5
360102 8PHIPPS B NP500.00 | 1.0554 | 1.0493 | OPEN LINE FROM BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1
360104 5VOLUNTEER#2161.00 | 1.0536 | 1.0456 | OPEN LINE FROM BUS 360104 [5VOLUNTEER#2161.00] TO BUS 360458 [5KNOX TN 161.00] CKT 2
360213 5MILLER MS 161.00 | 1.0526 | 1.0394 | OPEN LINE FROM BUS 361258 [5BYHALIA TAP161.00] TO BUS 361573 [5COLDWATR TP161.00] CKT 1
360339 5DAVIDSON #2161.00 | 1.0529 | 1.0491 | OPEN LINE FROM BUS 360339 [5DAVIDSON #2161.00] TO BUS 361179 [5GRASSLAND T161.00] CKT 1
360430 5HARRIMAN TN161.00 | 0.6581 | 1.0356 | OPEN LINE FROM BUS 360692 [5ROANE B#2 161.00] TO BUS 361383 [5W OAK RIDGT161.00] CKT 1
360447 5SOLWAY TN 161.00 | 0.9137 | 1.025 | OPEN LINE FROM BUS 360447 [5SOLWAY TN 161.00] TO BUS 361012 [5SOLWAY TN T161.00] CKT 1
360640 5JVILLE FP#3161.00 | 1.0541 | 1.0446 | OPEN LINE FROM BUS 360039 [5JVILLE FP#2161.00] TO BUS 360640 [5JVILLE FP#3161.00] CKT Z1
360643 5JVILLE CT#3161.00 | 1.0538 | 1.0442 | OPEN LINE FROM BUS 360039 [5JVILLE FP#2161.00] TO BUS 360640 [5JVILLE FP#3161.00] CKT Z1
360724 5FREEPORT #1161.00 | 1.0568 | 1.0495 | OPEN LINE FROM BUS 360024 [5FREEPORT TN161.00] TO BUS 360725 [5FREEPORT #2161.00] CKT Z1
360727 5CORDOVA #1T161.00 | 1.0562 | 1.0427 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361099 5BLAIR RD TP161.00 | 0.6543 | 1.0399 | OPEN LINE FROM BUS 360692 [5ROANE B#2 161.00] TO BUS 361383 [5W OAK RIDGT161.00] CKT 1
361146 5BLAIR RD TN161.00 | 0.6539 | 1.0396 | OPEN LINE FROM BUS 360692 [5ROANE B#2 161.00] TO BUS 361383 [5W OAK RIDGT161.00] CKT 1
361258 5BYHALIA TAP161.00 | 1.0521 | 1.0381 | OPEN LINE FROM BUS 361258 [5BYHALIA TAP161.00] TO BUS 361573 [5COLDWATR TP161.00] CKT 1
361316 5MURF INDPKT161.00 | 0.9433 | 1.0216 | OPEN LINE FROM BUS 360385 [5MURFREESBRO161.00] TO BUS 361316 [5MURF INDPKT161.00] CKT 1
361317 5MURF INDPK 161.00 | 0.9421 | 1.0205 | OPEN LINE FROM BUS 360385 [5MURFREESBRO161.00] TO BUS 361316 [5MURF INDPKT161.00] CKT 1
361383 5W OAK RIDGT161.00 | 0.6542 | 1.0401 | OPEN LINE FROM BUS 360692 [5ROANE B#2 161.00] TO BUS 361383 [5W OAK RIDGT161.00] CKT 1
361990 5VOLUNT KUB 161.00 | 1.0536 | 1.0456 | OPEN LINE FROM BUS 360104 [5VOLUNTEER#2161.00] TO BUS 360458 [5KNOX TN 161.00] CKT 2
380010 8FORTSON 500.00 | 1.0522 | 1.0426 | OPEN LINE FROM BUS 380010 [8FORTSON 500.00] TO BUS 380125 [6FORTSON LS 230.00] CKT 1
380015 8THALMANN 500.00 | 1.057 | 1.0464 | OPEN LINE FROM BUS 380009 [8W MCINTOSH 500.00] TO BUS 382158 [8MCCALL RD 500.00] CKT 1
380024 8N TIFTON 500.00 | 1.0533 | 1.0401 | OPEN LINE FROM BUS 380024 [8N TIFTON 500.00] TO BUS 380222 [6N TIFTON LS230.00] CKT 1
382158 8MCCALL RD 500.00 | 1.0718 | 1.0364 | OPEN LINE FROM BUS 380009 [8W MCINTOSH 500.00] TO BUS 382158 [8MCCALL RD 500.00] CKT 1
382804 6AL-GA LINE 230.00 | 1.0538 | 1.0378 | OPEN LINE FROM BUS 380179 [6ROOPVILLE 230.00] TO BUS 382804 [6AL-GA LINE 230.00] CKT 1
384375 8S.BESS 8 500.00 | 1.0526 | 1.0445 | OPEN LINE FROM BUS 384374 [6S.BESS 6 230.00] TO BUS 384375 [8S.BESS 8 500.00] CKT 1
384512 8SNOWDN8 500.00 | 1.053 | 1.0453 | OPEN LINE FROM BUS 384511 [6SNOWDN6 230.00] TO BUS 384512 [8SNOWDN8 500.00] CKT 1
385312 8CLAY 8 500.00 | 1.0523 | 1.0469 | OPEN LINE FROM BUS 384234 [6CLAY 6 230.00] TO BUS 385312 [8CLAY 8 500.00] CKT 1
388700 8DANIEL8 500.00 | 1.0747 | 1.0407 | OPEN LINE FROM BUS 388700 [8DANIEL8 500.00] TO BUS 388702 [6DANIEL6 230.00] CKT 1
389104 3ELBA ISL B1115.00 | 0.9466 | 0.9661 | OPEN LINE FROM BUS 389001 [6MCINTOSH 230.00] TO BUS 389176 [6CROSSGATE 230.00] CKT 1
389106 3WILMNGTN 115.00 | 0.946 | 0.9655 | OPEN LINE FROM BUS 389001 [6MCINTOSH 230.00] TO BUS 389176 [6CROSSGATE 230.00] CKT 1
389179 3ELBA ISL B2115.00 | 0.9466 | 0.9661 | OPEN LINE FROM BUS 389001 [6MCINTOSH 230.00] TO BUS 389176 [6CROSSGATE 230.00] CKT 1

## FRCC_N-1_VOLTAGE_SUM
BUS | VCONT pu | VINIT pu | CONTINGENCY
400005 FLACITY 230.00 | 0.8819 | 1.0058 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400010 JWFISHCK 138.00 | 0.8089 | 1.0205 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400040 FLA CITY 138.00 | 0.9259 | 1.0395 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400066 LUCY 138.00 | 0.9287 | 1.0359 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400103 AVENTURA 230.00 | 0.9462 | 1.0044 | OPEN LINE FROM BUS 400156 [MOFFETT 230.00] TO BUS 400182 [LAUDANIA 230.00] CKT 1
400107 GREYNOLD 230.00 | 0.948 | 0.9996 | OPEN LINE FROM BUS 400156 [MOFFETT 230.00] TO BUS 400182 [LAUDANIA 230.00] CKT 1
400110 LINDGREN 230.00 | 0.9483 | 0.9908 | OPEN LINE FROM BUS 400110 [LINDGREN 230.00] TO BUS 400119 [TURKEY P 230.00] CKT 1
400112 MIA EAST 230.00 | 0.9371 | 0.9648 | OPEN LINE FROM BUS 400727 [LATN QTR 230.00] TO BUS 400924 [8TH_STREET 230.00] CKT 1
400113 MIA WEST 230.00 | 0.9362 | 0.9678 | OPEN LINE FROM BUS 400106 [FLAGAMI 230.00] TO BUS 400113 [MIA WEST 230.00] CKT 1
400114 MIA SH 230.00 | 0.9474 | 0.9675 | OPEN LINE FROM BUS 400104 [DADE 230.00] TO BUS 400114 [MIA SH 230.00] CKT 1
400124 TRIGAS 230.00 | 0.9474 | 1.0028 | OPEN LINE FROM BUS 400582 [BRIDGE 230.00] TO BUS 400613 [ALEXANDR 230.00] CKT 1
400156 MOFFETT 230.00 | 0.9452 | 1.0094 | OPEN LINE FROM BUS 400156 [MOFFETT 230.00] TO BUS 400182 [LAUDANIA 230.00] CKT 1
400274 CORBETT 500.00 | 1.0545 | 1.0479 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400275 MARTIN 500.00 | 1.0589 | 1.0516 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400276 MIDWAY 500.00 | 1.0651 | 1.0453 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400298 COCOPLUM 138.00 | 0.9453 | 1.0037 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400304 ENGLEWOD 138.00 | 0.9236 | 1.0018 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400308 FRTVILLE 230.00 | 0.9476 | 0.9962 | OPEN LINE FROM BUS 400308 [FRTVILLE 230.00] TO BUS 400352 [RINGLING 230.00] CKT 1
400319 MYAKKA 138.00 | 0.919 | 1.0037 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400339 ROTONDA 138.00 | 0.9098 | 0.9953 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400345 GRANADA 230.00 | 0.8454 | 0.9804 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400347 KEENTOWN 230.00 | 1.0527 | 1.0393 | OPEN LINE FROM BUS 401006 [SUNSHINE 230.00] TO BUS 406899 [PINE LEVEL 230.00] CKT 1
400349 MANATEE 230.00 | 1.0533 | 1.0509 | OPEN LINE FROM BUS 400189 [ANDYTOWN 500.00] TO BUS 400354 [ORANGE R 500.00] CKT 1
400350 MYAKKA 230.00 | 0.8529 | 0.9736 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400475 YULEE 230.00 | 1.0628 | 1.0394 | OPEN LINE FROM BUS 400475 [YULEE 230.00] TO BUS 380166 [6KINGSLND B1230.00] CKT 1
400476 POINSETT 500.00 | 1.0809 | 1.0604 | OPEN LINE FROM BUS 400467 [POINSETT 230.00] TO BUS 400476 [POINSETT 500.00] CKT 1
400477 RICE 500.00 | 1.054 | 1.0408 | OPEN LINE FROM BUS 400468 [PUTNAM 230.00] TO BUS 400501 [ROBERTS 230.00] CKT 1
400484 ROBERTS 500.00 | 1.0615 | 1.037 | OPEN LINE FROM BUS 400484 [ROBERTS 500.00] TO BUS 400501 [ROBERTS 230.00] CKT 1
400501 ROBERTS 230.00 | 1.0887 | 1.0421 | OPEN LINE FROM BUS 400468 [PUTNAM 230.00] TO BUS 400501 [ROBERTS 230.00] CKT 1
400514 BASSCRK 230.00 | 0.9456 | 1.0054 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400516 [CHAPEL 230.00] CKT 1
400516 CHAPEL 230.00 | 0.9432 | 1.0237 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400516 [CHAPEL 230.00] CKT 1
400520 CROSSBOW 230.00 | 0.9395 | 1.0165 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400520 [CROSSBOW 230.00] CKT 1
400522 SHERIDAN 230.00 | 0.9402 | 1.0018 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400520 [CROSSBOW 230.00] CKT 1
400523 SILVRLK 230.00 | 0.9448 | 1.0108 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400516 [CHAPEL 230.00] CKT 1
400535 CORBETT 230.00 | 1.0536 | 1.0485 | OPEN LINE FROM BUS 400535 [CORBETT 230.00] TO BUS 401077 [COCUSTAP 230.00] CKT 1
400552 AUBURN 230.00 | 0.842 | 0.9864 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400567 HNTINGTN 230.00 | 0.9471 | 1.0012 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400516 [CHAPEL 230.00] CKT 1
400599 MILLS 230.00 | 1.0521 | 1.0359 | OPEN LINE FROM BUS 400475 [YULEE 230.00] TO BUS 380166 [6KINGSLND B1230.00] CKT 1
400613 ALEXANDR 230.00 | 0.9476 | 1.003 | OPEN LINE FROM BUS 400582 [BRIDGE 230.00] TO BUS 400613 [ALEXANDR 230.00] CKT 1
400712 ONEIL 230.00 | 1.062 | 1.0385 | OPEN LINE FROM BUS 400475 [YULEE 230.00] TO BUS 380166 [6KINGSLND B1230.00] CKT 1
400727 LATN QTR 230.00 | 0.937 | 0.9659 | OPEN LINE FROM BUS 400727 [LATN QTR 230.00] TO BUS 400924 [8TH_STREET 230.00] CKT 1
400732 MCGREGOR 230.00 | 0.8817 | 1.0275 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400739 GATOR 115.00 | 0.9478 | 1.0026 | OPEN LINE FROM BUS 400841 [MILLCREK 230.00] TO BUS 400840 [MILLCREK 115.00] CKT 1
400818 CORTEZ 230.00 | 0.9303 | 0.9907 | OPEN LINE FROM BUS 400346 [JOHNSON 230.00] TO BUS 400818 [CORTEZ 230.00] CKT 1
400840 MILLCREK 115.00 | 0.9386 | 1.0145 | OPEN LINE FROM BUS 400841 [MILLCREK 230.00] TO BUS 400840 [MILLCREK 115.00] CKT 1
400842 ANHINGA 138.00 | 0.9432 | 1.0409 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400856 SUGAR-REACT 230.00 | 1.0524 | 1.048 | OPEN LINE FROM BUS 400535 [CORBETT 230.00] TO BUS 401077 [COCUSTAP 230.00] CKT 1
400857 DURBIN 115.00 | 0.9418 | 0.9981 | OPEN LINE FROM BUS 400841 [MILLCREK 230.00] TO BUS 400840 [MILLCREK 115.00] CKT 1
400870 KEYLARGO 138.00 | 0.7862 | 1.0206 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400871 TAVRNIER 138.00 | 0.7658 | 1.0191 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400872 ISLMRADA 138.00 | 0.8282 | 0.9884 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400873 MARATHON 138.00 | 0.6227 | 0.9817 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400877 CRAWLKEY 138.00 | 0.7109 | 0.9763 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400879 ISLMRDASCAP 138.00 | 0.7101 | 1.0264 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400942 GRAHAM N EAS230.00 | 0.9484 | 0.9853 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400520 [CROSSBOW 230.00] CKT 1
400945 GALLOWAY 230.00 | 0.9178 | 0.9702 | OPEN LINE FROM BUS 400839 [GALTAP 230.00] TO BUS 400945 [GALLOWAY 230.00] CKT 1
400947 RIVERTON 115.00 | 0.9318 | 1.0083 | OPEN LINE FROM BUS 400841 [MILLCREK 230.00] TO BUS 400840 [MILLCREK 115.00] CKT 1
400957 GRAHAM S EAS230.00 | 0.9485 | 0.9852 | OPEN LINE FROM BUS 400175 [ANDYTOWN 230.00] TO BUS 400520 [CROSSBOW 230.00] CKT 1
400988 OVERTOWN 230.00 | 0.9401 | 0.9637 | OPEN LINE FROM BUS 400104 [DADE 230.00] TO BUS 400988 [OVERTOWN 230.00] CKT 1
400991 MAR1COLL 500.00 | 1.0588 | 1.0515 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400992 MAR2COLL 500.00 | 1.0588 | 1.0515 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400993 MNT1COLL 230.00 | 1.0535 | 1.0511 | OPEN LINE FROM BUS 400189 [ANDYTOWN 500.00] TO BUS 400354 [ORANGE R 500.00] CKT 1
400994 MNT2COLL 230.00 | 1.0534 | 1.051 | OPEN LINE FROM BUS 400189 [ANDYTOWN 500.00] TO BUS 400354 [ORANGE R 500.00] CKT 1
401009 COAST 230.00 | 0.9295 | 0.9925 | OPEN LINE FROM BUS 401007 [PEACHLND 230.00] TO BUS 401009 [COAST 230.00] CKT 1
401030 MR REACT 230.00 | 1.053 | 1.0194 | OPEN LINE FROM BUS 400275 [MARTIN 500.00] TO BUS 401030 [MR REACT 230.00] CKT 1
401053 MCCALL 138.00 | 0.9116 | 0.9969 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
401074 CORBETTCUST 230.00 | 1.0535 | 1.0485 | OPEN LINE FROM BUS 400268 [RANCH 230.00] TO BUS 401077 [COCUSTAP 230.00] CKT 1
401075 FLCYDIS 138.00 | 0.926 | 1.0393 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
401077 COCUSTAP 230.00 | 1.0535 | 1.0485 | OPEN LINE FROM BUS 400268 [RANCH 230.00] TO BUS 401077 [COCUSTAP 230.00] CKT 1
401135 LRLWDISTTP 230.00 | 0.843 | 0.9917 | OPEN LINE FROM BUS 400348 [LAURELWD 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
401199 AVENDUMY 230.00 | 0.9483 | 0.9999 | OPEN LINE FROM BUS 400156 [MOFFETT 230.00] TO BUS 400182 [LAUDANIA 230.00] CKT 1
401206 MR8 AUX1 230.00 | 1.0546 | 1.0462 | OPEN LINE FROM BUS 401030 [MR REACT 230.00] TO BUS 401520 [MARTN2 230.00] CKT 1
401207 MR8 AUX2 230.00 | 1.0548 | 1.0466 | OPEN LINE FROM BUS 400275 [MARTIN 500.00] TO BUS 401030 [MR REACT 230.00] CKT 1
401216 MN3 AUX1 230.00 | 1.0536 | 1.0511 | OPEN LINE FROM BUS 400351 [ORANGE R 230.00] TO BUS 400354 [ORANGE R 500.00] CKT 1
401217 MN3 AUX2 230.00 | 1.0535 | 1.0511 | OPEN LINE FROM BUS 400351 [ORANGE R 230.00] TO BUS 400354 [ORANGE R 500.00] CKT 1
401311 WCE1-CL1 230.00 | 1.0551 | 1.0502 | OPEN LINE FROM BUS 400535 [CORBETT 230.00] TO BUS 401077 [COCUSTAP 230.00] CKT 1
401312 WCE1-CL2 230.00 | 1.0552 | 1.0503 | OPEN LINE FROM BUS 400535 [CORBETT 230.00] TO BUS 401077 [COCUSTAP 230.00] CKT 1
401331 WC2 AUX1 500.00 | 1.0547 | 1.0482 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
401332 WC2 AUX2 500.00 | 1.0547 | 1.0482 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
401351 MCCALLTP 138.00 | 0.9139 | 0.999 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
401520 MARTN2 230.00 | 1.053 | 1.0444 | OPEN LINE FROM BUS 400275 [MARTIN 500.00] TO BUS 401030 [MR REACT 230.00] CKT 1
402583 MEADOW WD S 230.00 | 0.9313 | 1.0024 | OPEN LINE FROM BUS 402583 [MEADOW WD S 230.00] TO BUS 405704 [TAFT 230.00] CKT 1
402587 SKY LAKE 230.00 | 0.9317 | 0.9841 | OPEN LINE FROM BUS 402587 [SKY LAKE 230.00] TO BUS 405701 [SO WOOD 230.00] CKT 1
402884 KATHLEEN 230.00 | 0.9439 | 0.9942 | OPEN LINE FROM BUS 402271 [GRIFFIN 230.00] TO BUS 402884 [KATHLEEN 230.00] CKT 1
403170 WILCOX 230.00 | 0.9365 | 0.9998 | OPEN LINE FROM BUS 403165 [NEWBERRY 230.00] TO BUS 403170 [WILCOX 230.00] CKT 1
403799 OVERSTREETTP115.00 | 0.8145 | 1.0023 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
403816 ZEPHYRHLLS N115.00 | 0.8147 | 1.0313 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
403817 NEW RIVER 115.00 | 0.8206 | 0.9975 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
403835 NEW RIVER 230.00 | 0.9276 | 0.9809 | OPEN LINE FROM BUS 403835 [NEW RIVER 230.00] TO BUS 403838 [ZEPHYRHLLS N230.00] CKT 1
403838 ZEPHYRHLLS N230.00 | 0.9369 | 0.9844 | OPEN LINE FROM BUS 402271 [GRIFFIN 230.00] TO BUS 402884 [KATHLEEN 230.00] CKT 1
404476 HST-LUCY 138.00 | 0.9286 | 1.0357 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
404477 HST-MCMI 138.00 | 0.9289 | 1.035 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
404478 REDLAND 138.00 | 0.9272 | 1.0344 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
404479 RENAISSA 138.00 | 0.9279 | 1.035 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
405301 BIGPINE 138.00 | 0.5655 | 0.9944 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
405302 KEY BCS 138.00 | 0.5156 | 1.0046 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
405303 KEY SIS1 138.00 | 0.5117 | 1.0058 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
405304 KEY CKS 138.00 | 0.5401 | 0.997 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
405305 KEY SIS2 138.00 | 0.5087 | 1.0056 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
406299 OC SHAW 230.00 | 0.9461 | 0.9952 | OPEN LINE FROM BUS 406299 [OC SHAW 230.00] TO BUS 407120 [SLV_SP_N 230.00] CKT 1
406671 BLCK_S_115 115.00 | 1.0604 | 1.0442 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406673 BLCK_S_230 230.00 | 0.9487 | 1.014 | OPEN LINE FROM BUS 404780 [JAX HGTS 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT 1
406699 MIDDLBR. 115.00 | 1.056 | 1.0398 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406703 RDGWD TP 115.00 | 1.0525 | 1.0362 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406704 RIDGWOOD 115.00 | 1.0538 | 1.0375 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406705 RDGWD SW 115.00 | 1.0538 | 1.0375 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406750 BLCK_N_230 230.00 | 0.9487 | 1.014 | OPEN LINE FROM BUS 404780 [JAX HGTS 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT 1
406899 PINE LEVEL 230.00 | 1.0533 | 1.0285 | OPEN LINE FROM BUS 401006 [SUNSHINE 230.00] TO BUS 406899 [PINE LEVEL 230.00] CKT 1
407098 ELAM 115.00 | 0.8063 | 0.9957 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
407100 ELAM TP 115.00 | 0.809 | 0.9979 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
407113 OVERSTREET 115.00 | 0.8145 | 1.0023 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
407431 STC EAST 230.00 | 0.9367 | 1.0155 | OPEN LINE FROM BUS 402882 [HOLOPAW 1 230.00] TO BUS 407431 [STC EAST 230.00] CKT 1
407432 STC SOU 230.00 | 0.9355 | 1.0102 | OPEN LINE FROM BUS 402882 [HOLOPAW 1 230.00] TO BUS 407431 [STC EAST 230.00] CKT 1
408301 GANNON-RX230230.00 | 1.0522 | 1.0522 | BASE CASE BASE CASE
408700 GANNON 230.00 | 1.0522 | 1.0522 | BASE CASE BASE CASE
409807 SO CAPE 138.00 | 0.9473 | 1.0065 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409810 CP CORAL 138.00 | 0.9396 | 0.9994 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409824 PN ISL 138.00 | 0.945 | 1.0044 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409826 SANIBEL 138.00 | 0.9387 | 0.9986 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409829 CP CL TP 138.00 | 0.9426 | 1.0022 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409830 SO CP TP 138.00 | 0.9396 | 0.9994 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1