## NPCC_N-1_VOLTAGE_WINTER
BUS | VCONT | VINIT | CONTINGENCY | COMMENTS
100001 CHESTER SVC 345.00 | 1.0543 | 1.0349 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
100004 ORRNGTN SCAP345.00 | 1.0638 | 1.0432 | OPEN LINE FROM BUS 100002 [ORRINGTON 345.00] TO BUS 100004 [ORRNGTN SCAP345.00] CKT 1
100005 COOPERS MILL345.00 | 1.0553 | 1.0491 | OPEN LINE FROM BUS 190572 [BELLDTX 345.00] TO BUS 190472 [BLLDNG2 19.000] CKT 1
100050 EM_396_MPCO 345.00 | 1.0546 | 1.035 | OPEN LINE FROM BUS 100050 [EM_396_MPCO 345.00] TO BUS 103001 [KEENE ROAD 345.00] CKT 1
100051 EM_3001_MCO 345.00 | 1.0543 | 1.035 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
100086 MAINE YANKEE345.00 | 1.0554 | 1.0496 | OPEN LINE FROM BUS 190399 [BELLDUBS 345.00] TO BUS 190572 [BELLDTX 345.00] CKT 1
100087 SUROWIEC 345.00 | 1.0527 | 1.0479 | OPEN LINE FROM BUS 190399 [BELLDUBS 345.00] TO BUS 190572 [BELLDTX 345.00] CKT 1
100091 MASON 345.00 | 1.0553 | 1.0495 | OPEN LINE FROM BUS 190399 [BELLDUBS 345.00] TO BUS 190572 [BELLDTX 345.00] CKT 1
100092 ALBION ROAD 345.00 | 1.0556 | 1.0494 | OPEN LINE FROM BUS 100002 [ORRINGTON 345.00] TO BUS 100004 [ORRNGTN SCAP345.00] CKT 1
100095 LARRABEE RD 345.00 | 1.0555 | 1.0501 | OPEN LINE FROM BUS 190399 [BELLDUBS 345.00] TO BUS 190572 [BELLDTX 345.00] CKT 1
103001 KEENE ROAD 345.00 | 1.0543 | 1.035 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103011 COLUMBIA_T 115.00 | 1.0522 | 1.0517 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103020 DEBLOIS 115.00 | 1.0526 | 1.0522 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 103001 [KEENE ROAD 345.00] CKT 1
103021 EPPING TAP 115.00 | 1.0536 | 1.0531 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103029 POWERSVILLE 115.00 | 1.0523 | 1.0398 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103030 TRENTON 115.00 | 1.0524 | 1.0518 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103031 STETSON WIND115.00 | 1.0572 | 1.0417 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 103001 [KEENE ROAD 345.00] CKT 1
103085 ROLLINS TAP 115.00 | 1.055 | 1.0395 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103086 ROLLINS WIND115.00 | 1.0554 | 1.04 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103091 BULL HILL 115.00 | 1.0515 | 1.0511 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103094 TRENTON_C 115.00 | 1.0524 | 1.0518 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103095 EPPING TAP_C115.00 | 1.0536 | 1.0531 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103100 MILLNCKT 4 115.00 | 1.0519 | 1.0398 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 103001 [KEENE ROAD 345.00] CKT 1
103101 MCKAY HYDRO 115.00 | 1.0564 | 1.044 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
103142 OAKFIELD_POI115.00 | 1.0558 | 1.0378 | OPEN LINE FROM BUS 100001 [CHESTER SVC 345.00] TO BUS 100318 [CHESTER SVC 18.000] CKT 1
104151 LAWRENCE RD 345.00 | 1.0523 | 1.0438 | OPEN LINE FROM BUS 104143 [SCOBIE POND 345.00] TO BUS 104151 [LAWRENCE RD 345.00] CKT 1
104159 NU_326_NGR 345.00 | 1.0531 | 1.0461 | OPEN LINE FROM BUS 104151 [LAWRENCE RD 345.00] TO BUS 104159 [NU_326_NGR 345.00] CKT 1
106016 SLAYTON HILL115.00 | 0.9443 | 0.9533 | OPEN LINE FROM BUS 106012 [N.LITCHFLD1 230.00] TO BUS 113955 [TEWKSBURY 230.00] CKT 1
106020 MT SUPPORT 115.00 | 0.9436 | 0.9537 | OPEN LINE FROM BUS 106012 [N.LITCHFLD1 230.00] TO BUS 113955 [TEWKSBURY 230.00] CKT 1
109572 WILDER 115.00 | 0.9498 | 0.9602 | OPEN LINE FROM BUS 106012 [N.LITCHFLD1 230.00] TO BUS 113955 [TEWKSBURY 230.00] CKT 1
109600 NGR_K26_VEL 115.00 | 0.9498 | 0.9602 | OPEN LINE FROM BUS 106012 [N.LITCHFLD1 230.00] TO BUS 113955 [TEWKSBURY 230.00] CKT 1
110789 WALTHAM 230.00 | 1.0636 | 1.0277 | OPEN LINE FROM BUS 110789 [WALTHAM 230.00] TO BUS 110810 [WALTHAM PS 115.00] CKT 1
110793 W MEDWAY B 230.00 | 1.0615 | 1.0472 | OPEN LINE FROM BUS 110795 [FRAMINGHAM 230.00] TO BUS 110870 [FRAMINGHAM 115.00] CKT 1
110794 W MEDWAY A 230.00 | 1.0622 | 1.0508 | OPEN LINE FROM BUS 110789 [WALTHAM 230.00] TO BUS 110810 [WALTHAM PS 115.00] CKT 1
110795 FRAMINGHAM 230.00 | 1.0617 | 1.0341 | OPEN LINE FROM BUS 110795 [FRAMINGHAM 230.00] TO BUS 110870 [FRAMINGHAM 115.00] CKT 1
113950 SANDY POND 345.00 | 1.0559 | 1.0497 | OPEN LINE FROM BUS 113950 [SANDY POND 345.00] TO BUS 113951 [TEWKSBURY 345.00] CKT 1
114071 SNDYPD HVDC1345.00 | 1.0562 | 1.05 | OPEN LINE FROM BUS 113950 [SANDY POND 345.00] TO BUS 113951 [TEWKSBURY 345.00] CKT 1
114072 SNDYPD HVDC2345.00 | 1.056 | 1.0498 | OPEN LINE FROM BUS 113950 [SANDY POND 345.00] TO BUS 113951 [TEWKSBURY 345.00] CKT 1
126250 RAMAPO 5 500.00 | 1.0788 | 1.0757 | OPEN LINE FROM BUS 126250 [RAMAPO 5 500.00] TO BUS 126296 [RAM PAR 345.00] CKT 1 | NYISO's comment : Local RR Exception
126272 E13ST 45 345.00 | 1.0554 | 1.0503 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's comment : Operator Action
126273 E13ST 46 345.00 | 1.0557 | 1.0505 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's comment : Local RR Exception
126274 E13ST 47 345.00 | 1.055 | 1.0494 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126275 E13ST 48 345.00 | 1.055 | 1.0494 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126277 FARRAGUT 345.00 | 1.0552 | 1.05 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126278 B3402 PAR1 345.00 | 1.055 | 1.0528 | OPEN LINE FROM BUS 126278 [B3402 PAR1 345.00] TO BUS 126645 [FARRAGUT EAS345.00] CKT 1
126279 C3403 PAR2 345.00 | 1.0549 | 1.0528 | OPEN LINE FROM BUS 126279 [C3403 PAR2 345.00] TO BUS 126644 [FARRAGUT WES345.00] CKT 1
126280 FARRAGUT TX9345.00 | 1.0951 | 1.05 | OPEN LINE FROM BUS 126280 [FARRAGUT TX9345.00] TO BUS 126645 [FARRAGUT EAS345.00] CKT 1
126291 MILLWOOD 345.00 | 1.0518 | 1.0473 | SB:LADE_3-56-2 OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 146775 [WHAV138 138.00] CKT 1OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 126260 [BOWLINE1 345.00] CKT 10 OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 126290 [LADENTWN 345.00] CKT 1OPEN LINE FROM BUS 146841 [BOW1 20.000] TO BUS 126260 [BOWLINE1 345.00] CKT 1TRIP BRANCH FROM BUS 126290 [LADENTWN 345.00] TO BUS 126263 [BUCHANAN S 345.00] CKT 1
126295 RAINEY 345.00 | 1.0544 | 1.0497 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126298 SPRAINBROOK 345.00 | 1.0509 | 1.0469 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126301 TREMONT 345.00 | 1.0506 | 1.0466 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126304 W 49 ST 345.00 | 1.0565 | 1.0515 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126398 FGT_Y9 138.00 | 1.057 | 1.0136 | OPEN LINE FROM BUS 126280 [FARRAGUT TX9345.00] TO BUS 126398 [FGT_Y9 138.00] CKT 1 | NYISO's comment : Local RR Exception
126482 RAINEY9E 138.00 | 1.1211 | 1.0093 | OPEN LINE FROM BUS 126295 [RAINEY 345.00] TO BUS 126563 [9E DUM 138.00] CKT 1
126484 SEAPT 5&9 138.00 | 1.0569 | 1.0137 | OPEN LINE FROM BUS 126280 [FARRAGUT TX9345.00] TO BUS 126398 [FGT_Y9 138.00] CKT 1
126488 38M15 TAP 138.00 | 1.0569 | 1.0137 | OPEN LINE FROM BUS 126280 [FARRAGUT TX9345.00] TO BUS 126398 [FGT_Y9 138.00] CKT 1
126495 T14MPT 138.00 | 1.0518 | 1.0466 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126499 T11MPT 138.00 | 1.0614 | 1.0557 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126501 TRADE TX3 138.00 | 1.0568 | 1.0137 | OPEN LINE FROM BUS 126280 [FARRAGUT TX9345.00] TO BUS 126398 [FGT_Y9 138.00] CKT 1
126517 REACM51 345.00 | 1.0509 | 1.0469 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126518 REACM52 345.00 | 1.0509 | 1.0469 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126534 W110 5&9 138.00 | 1.1204 | 1.0092 | OPEN LINE FROM BUS 126295 [RAINEY 345.00] TO BUS 126563 [9E DUM 138.00] CKT 1
126539 W42 T1&9 138.00 | 0.9472 | 1.0149 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126547 W49 ST 5 138.00 | 0.9472 | 1.0152 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126548 ASTOR T3 TAP138.00 | 0.9473 | 1.0151 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126553 W65ST1&6 138.00 | 0.9472 | 1.0147 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126563 9E DUM 138.00 | 1.1211 | 0.9978 | OPEN LINE FROM BUS 126295 [RAINEY 345.00] TO BUS 126563 [9E DUM 138.00] CKT 1
126590 GOWANUS 41SR345.00 | 1.0545 | 1.0494 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126591 GOWANUS 42SR345.00 | 1.0545 | 1.0494 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126599 W42 TX9 138.00 | 0.9472 | 1.0148 | SB:W49_8 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1TRIP BRANCH FROM BUS 126547 [W49 ST 5 138.00] TO BUS 126304 [W 49 ST 345.00] CKT 1
126600 REAC71 345.00 | 1.0542 | 1.0469 | OPEN LINE FROM BUS 126266 [DUNWOODIE 345.00] TO BUS 126600 [REAC71 345.00] CKT BY
126601 REAC72 345.00 | 1.0543 | 1.0469 | OPEN LINE FROM BUS 126266 [DUNWOODIE 345.00] TO BUS 126601 [REAC72 345.00] CKT BY
126641 MOTT HAVEN 345.00 | 1.0541 | 1.0495 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126642 RAINEY WEST 345.00 | 1.0544 | 1.0497 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126643 RAINEY EAST 345.00 | 1.0544 | 1.0497 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126644 FARRAGUT WES345.00 | 1.0552 | 1.05 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126645 FARRAGUT EAS345.00 | 1.0552 | 1.05 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126819 RN-CR PAR 138.00 | 0.9179 | 0.9259 | S:HTP_DC31 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 94130 [O66_NONFIRM 230.00] CKT 1 OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 217100 [BERGEN 230.00] CKT 1OPEN LINE FROM BUS 219811 [O66_HUDSNDC 230.00] TO BUS 219810 [CNV_BRG 77.000] CKT 1OPEN LINE FROM BUS 217177 [CNV_BRG2 77.000] TO BUS 217178 [Q206_HUDSNDC345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 126304 [W 49 ST 345.00] CKT 1OPEN LINE FROM BUS 217178 [Q206_HUDSNDC345.00] TO BUS 128819 [HDSN_NONFIRM345.00] CKT 1 | NYISO's comment :Operator Action
126847 ACADEMY 345.00 | 1.0528 | 1.0488 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126865 RAV3 60M 345.00 | 1.0544 | 1.0496 | OPEN LINE FROM BUS 147829 [ASTOR345 345.00] TO BUS 148707 [Q308_AST2 345.00] CKT 1
126866 RAV3 60L 345.00 | 1.0544 | 1.0496 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
128248 ANNTRHIGH 345.00 | 1.0548 | 1.0479 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1 | NYISO's comment : Local RR Exception
128700 MILLW CAP 345.00 | 1.0518 | 1.0473 | SB:LADE_3-56-2 OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 146775 [WHAV138 138.00] CKT 1OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 126260 [BOWLINE1 345.00] CKT 10 OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 126290 [LADENTWN 345.00] CKT 1OPEN LINE FROM BUS 146841 [BOW1 20.000] TO BUS 126260 [BOWLINE1 345.00] CKT 1TRIP BRANCH FROM BUS 126290 [LADENTWN 345.00] TO BUS 126263 [BUCHANAN S 345.00] CKT 1
128701 ASTOR REAC 345.00 | 1.0548 | 1.0479 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
129324 BETHPAGE 138.00 | 1.0512 | 1.0502 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
130756 STOLE345 345.00 | 1.066 | 1.0051 | S:STOLLE345 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 1 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 2 | NYISO's comment : Operator Action
130757 WATRC345 345.00 | 1.0608 | 1.0484 | SB:WATRC345_31-2 TRIP BRANCH FROM BUS 130755 [OAKDL345 345.00] TO BUS 130757 [WATRC345 345.00] CKT 1 TRIP BRANCH FROM BUS 130757 [WATRC345 345.00] TO BUS 130768 [WATRC230 230.00] CKT 2
130771 MADISONT 115.00 | 0.9347 | 0.9423 | SB:OAKD345_36-B222 TRIP BRANCH FROM BUS 130755 [OAKDL345 345.00] TO BUS 131157 [CLARKCRNS 345.00] CKT 1 OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130755 [OAKDL345 345.00] CKT 1OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130838 [OAKDL115 115.00] CKT 1
130778 BROTH115 115.00 | 0.9348 | 0.9423 | SB:OAKD345_36-B222 TRIP BRANCH FROM BUS 130755 [OAKDL345 345.00] TO BUS 131157 [CLARKCRNS 345.00] CKT 1 OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130755 [OAKDL345 345.00] CKT 1OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130838 [OAKDL115 115.00] CKT 1
130779 C.LIN115 115.00 | 0.9339 | 0.9421 | SB:OAKD345_36-B222 TRIP BRANCH FROM BUS 130755 [OAKDL345 345.00] TO BUS 131157 [CLARKCRNS 345.00] CKT 1 OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130755 [OAKDL345 345.00] CKT 1OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130838 [OAKDL115 115.00] CKT 1
130796 E.NOR115 115.00 | 0.9362 | 0.9449 | SB:OAKD345_36-B222 TRIP BRANCH FROM BUS 130755 [OAKDL345 345.00] TO BUS 131157 [CLARKCRNS 345.00] CKT 1 OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130755 [OAKDL345 345.00] CKT 1OPEN LINE FROM BUS 130839 [OAK2M115 115.00] TO BUS 130838 [OAKDL115 115.00] CKT 1
135398 SW345 345.00 | 1.0597 | 1.0254 | S:STOLLE345 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 1 TRIP BRANCH FROM BUS 130756 [STOLE345 345.00] TO BUS 130857 [STOLE115 115.00] CKT 2
135411 ELM-71 230.00 | 0.9082 | 0.9866 | OPEN LINE FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135416 [SENCA-71 230.00] CKT 1
135412 ELM-72 230.00 | 0.8849 | 0.9866 | SB:GARD230_R823 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135450 [GRDNVL1 115.00] CKT 3 TRIP BRANCH FROM BUS 135418 [SUNY-79 230.00] TO BUS 135413 [GRDNVL2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135306 [SAWYER79 230.00] CKT 1 TRIP BRANCH FROM BUS 135306 [SAWYER79 230.00] TO BUS 135418 [SUNY-79 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135417 [SENCA-72 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 130762 [GARDV230 230.00] CKT 1
135416 SENCA-71 230.00 | 0.9078 | 0.9866 | OPEN LINE FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135416 [SENCA-71 230.00] CKT 1
135417 SENCA-72 230.00 | 0.8845 | 0.9866 | SB:GARD230_R823 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135450 [GRDNVL1 115.00] CKT 3 TRIP BRANCH FROM BUS 135418 [SUNY-79 230.00] TO BUS 135413 [GRDNVL2 230.00] CKT 1 TRIP BRANCH FROM BUS 135414 [HUNTLEY2 230.00] TO BUS 135306 [SAWYER79 230.00] CKT 1 TRIP BRANCH FROM BUS 135306 [SAWYER79 230.00] TO BUS 135418 [SUNY-79 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 135417 [SENCA-72 230.00] CKT 1 TRIP BRANCH FROM BUS 135413 [GRDNVL2 230.00] TO BUS 130762 [GARDV230 230.00] CKT 1
137201 FRAEDCSC 345.00 | 1.0549 | 1.0449 | SB:MARC345_3108 TRIP BRANCH FROM BUS 147833 [MARCY T1 345.00] TO BUS 137200 [EDIC 345.00] CKT 1 TRIP BRANCH FROM BUS 136156 [VOLNEY 345.00] TO BUS 147833 [MARCY T1 345.00] CKT 1
137927 RECTOR 230.00 | 1.0543 | 1.0454 | SB:ADIR_230_214 TRIP BRANCH FROM BUS 147835 [ADRON B1 230.00] TO BUS 137928 [CHASES L 230.00] CKT 1 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1
147828 MASS 765 765.00 | 1.0684 | 1.0109 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
147829 ASTOR345 345.00 | 1.0548 | 1.0479 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
147832 IP3 345 345.00 | 1.0513 | 1.0442 | SB:LADE_3-56-2 OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 146775 [WHAV138 138.00] CKT 1OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 126260 [BOWLINE1 345.00] CKT 10 OPEN LINE FROM BUS 146750 [WHAV345 345.00] TO BUS 126290 [LADENTWN 345.00] CKT 1OPEN LINE FROM BUS 146841 [BOW1 20.000] TO BUS 126260 [BOWLINE1 345.00] CKT 1TRIP BRANCH FROM BUS 126290 [LADENTWN 345.00] TO BUS 126263 [BUCHANAN S 345.00] CKT 1
147833 MARCY T1 345.00 | 1.0586 | 1.0333 | SB:MARC345_3108 TRIP BRANCH FROM BUS 147833 [MARCY T1 345.00] TO BUS 137200 [EDIC 345.00] CKT 1 TRIP BRANCH FROM BUS 136156 [VOLNEY 345.00] TO BUS 147833 [MARCY T1 345.00] CKT 1
147835 ADRON B1 230.00 | 1.0565 | 1.0417 | T:MAP1&2 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147835 [ADRON B1 230.00] CKT 1 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1 TRIP BRANCH FROM BUS 137210 [PORTER 2 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1
147836 ADRON B2 230.00 | 1.0565 | 1.0417 | T:MAP1&2 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147835 [ADRON B1 230.00] CKT 1 TRIP BRANCH FROM BUS 147840 [MOSES W 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1 TRIP BRANCH FROM BUS 137210 [PORTER 2 230.00] TO BUS 147836 [ADRON B2 230.00] CKT 1
147837 MASS230A 230.00 | 1.1055 | 1.0235 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
147838 MASS230B 230.00 | 1.1055 | 1.0235 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
148049 USTATCOM 345.00 | 1.0586 | 1.0333 | SB:MARC345_3108 TRIP BRANCH FROM BUS 147833 [MARCY T1 345.00] TO BUS 137200 [EDIC 345.00] CKT 1 TRIP BRANCH FROM BUS 136156 [VOLNEY 345.00] TO BUS 147833 [MARCY T1 345.00] CKT 1
148059 MARCCSC1 345.00 | 1.0569 | 1.0447 | T:34&42A_CE18/UC30 TRIP BRANCH FROM BUS 148995 [CPV_VALY 345.00] TO BUS 130750 [COOPC345 345.00] CKT 2 OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 146772 [SHOEMTAP 138.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 125001 [ROCK TAV 345.00] CKT 1OPEN LINE FROM BUS 146754 [MDTN TAP 345.00] TO BUS 130750 [COOPC345 345.00] CKT 1
148060 MARCCSC2 345.00 | 1.0609 | 1.0369 | SB:MARC345_3108 TRIP BRANCH FROM BUS 147833 [MARCY T1 345.00] TO BUS 137200 [EDIC 345.00] CKT 1 TRIP BRANCH FROM BUS 136156 [VOLNEY 345.00] TO BUS 147833 [MARCY T1 345.00] CKT 1
148707 Q308_AST2 345.00 | 1.0548 | 1.0476 | G:SCS_AST_2 OPEN LINE FROM BUS 148708 [Q308_GT1 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148709 [Q308_GT2 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1OPEN LINE FROM BUS 148710 [Q308_ST 18.000] TO BUS 148707 [Q308_AST2 345.00] CKT 1
148720 MARCY CAP 345.00 | 1.0586 | 1.0333 | SB:MARC345_3108 TRIP BRANCH FROM BUS 147833 [MARCY T1 345.00] TO BUS 137200 [EDIC 345.00] CKT 1 TRIP BRANCH FROM BUS 136156 [VOLNEY 345.00] TO BUS 147833 [MARCY T1 345.00] CKT 1
148721 MASS REAC 765.00 | 1.0684 | 1.0109 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
148721 MASS REAC 765.00 | 0.9259 | 1.0109 | SB:MARC_765_7402 TRIP BRANCH FROM BUS 147828 [MASS 765 765.00] TO BUS 180819 [CHA-NY 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147828 [MASS 765 765.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 1 TRIP BRANCH FROM BUS 147827 [MARCY765 765.00] TO BUS 147833 [MARCY T1 345.00] CKT 2
180302 DUV315 315.00 | 1.0726 | 1.0421 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
180309 ARN315 315.00 | 0.9437 | 0.9912 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
180317 JCA315 315.00 | 1.0611 | 1.0371 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
180409 ARN315 A315.00 | 0.9437 | 0.9912 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
180424 ROM4-315 315.00 | 1.0722 | 1.0606 | OPEN LINE FROM BUS 180310 [MTG315 315.00] TO BUS 180710 [MTG735 735.00] CKT 2
180427 NTDAME 315.00 | 1.0801 | 1.0481 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
180431 SAR315 315.00 | 1.0648 | 1.0331 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
180433 B1-315 315.00 | 0.897 | 0.959 | OPEN LINE FROM BUS 180441 [MANI5B 315.00] TO BUS 180241 [MAN-5B 13.800] CKT 1
180434 B2-315 315.00 | 0.9043 | 0.9682 | OPEN LINE FROM BUS 180434 [B2-315 315.00] TO BUS 180034 [BE2 13.800] CKT 1
180438 ATW315 315.00 | 0.937 | 1.0081 | OPEN LINE FROM BUS 180438 [ATW315 315.00] TO BUS 180463 [VIG315 315.00] CKT 1
180450 B_ST_PAUL315315.00 | 0.9395 | 0.9935 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
180451 CHVOI1 315.00 | 0.9249 | 0.9847 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
180452 CHVOI2 315.00 | 0.9249 | 0.9847 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
180460 BASQUE 315.00 | 0.8938 | 0.9608 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
180462 LAN315 315.00 | 1.0657 | 1.043 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
180471 DBLOOM 315.00 | 1.0551 | 1.0436 | OPEN LINE FROM BUS 180310 [MTG315 315.00] TO BUS 180710 [MTG735 735.00] CKT 2
180472 RDL315 315.00 | 1.0729 | 1.0534 | OPEN LINE FROM BUS 190420 [STANDR 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180473 RIM315 315.00 | 1.074 | 1.059 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180474 MTP315 315.00 | 1.0927 | 1.0815 | OPEN LINE FROM BUS 186460 [LEPLAT1-315E315.00] TO BUS 186462 [LEPLAT1--35E34.500] CKT 1
180475 LGL315 315.00 | 0.9451 | 1.0091 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180475 [LGL315 315.00] CKT 1
180476 LGL315 A315.00 | 0.9449 | 1.009 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
180477 NORMAN 315.00 | 1.0558 | 1.0443 | OPEN LINE FROM BUS 180310 [MTG315 315.00] TO BUS 180710 [MTG735 735.00] CKT 2
180488 MAURIC 315.00 | 1.0768 | 1.0568 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
180490 KAM<A> 315.00 | 1.1124 | 1.0855 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180490 KAM<A> 315.00 | 1.0855 | 1.0855 | BASE CASE BASE CASE
180491 KAM<B> 315.00 | 1.0855 | 1.0855 | BASE CASE BASE CASE
180492 KAM<C> 315.00 | 1.1308 | 1.1006 | OPEN LINE FROM BUS 190420 [STANDR 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180493 KAM<D> 315.00 | 1.1307 | 1.1006 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180494 KAM<E> 315.00 | 1.0682 | 1.0369 | OPEN LINE FROM BUS 180490 [KAM<A> 315.00] TO BUS 180494 [KAM<E> 315.00] CKT 1
180495 KAM<F> 315.00 | 1.0682 | 1.0369 | OPEN LINE FROM BUS 180491 [KAM<B> 315.00] TO BUS 180495 [KAM<F> 315.00] CKT 1
180496 KAM<G> 315.00 | 1.0759 | 1.0375 | OPEN LINE FROM BUS 180492 [KAM<C> 315.00] TO BUS 180496 [KAM<G> 315.00] CKT 1
180497 KAM<H> 315.00 | 1.0759 | 1.0375 | OPEN LINE FROM BUS 180493 [KAM<D> 315.00] TO BUS 180497 [KAM<H> 315.00] CKT 1
180526 OUTHAW 220.00 | 1.0816 | 1.0715 | OPEN LINE FROM BUS 154000 [HAWTHORNE_TS500.00] TO BUS 155000 [LENNOX_TS 500.00] CKT 1
180575 MADAWA 315.00 | 1.1155 | 1.0673 | OPEN LINE FROM BUS 190420 [STANDR 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
180626 CDP345 345.00 | 1.0632 | 1.062 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
180675 MADAWA A345.00 | 1.1469 | 1.0638 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
180819 CHA-NY 765.00 | 1.0697 | 1.0137 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
181119 CHANY1 120.00 | 1.1334 | 1.0765 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
181128 LBL120 120.00 | 1.0709 | 1.0554 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
181219 CHANY2 120.00 | 1.1334 | 1.0765 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
181227 NDM120 120.00 | 1.0732 | 1.0387 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
181228 BDL120 120.00 | 1.0954 | 1.0177 | OPEN LINE FROM BUS 180428 [BDL315 315.00] TO BUS 181228 [BDL120 120.00] CKT 8
181262 LAN120 120.00 | 1.0545 | 1.0299 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
181272 RDL120 120.00 | 1.0587 | 1.0283 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
181275 LGL120 120.00 | 0.9311 | 0.9786 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
181330 FIG120 120.00 | 1.0659 | 1.0654 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
181390 THE120 120.00 | 1.0588 | 1.0496 | OPEN LINE FROM BUS 180790 [APA735 735.00] TO BUS 182090 [APA230 230.00] CKT 2
181419 CHATG4 120.00 | 1.1298 | 1.0729 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
181454 R15EXP 120.00 | 1.0637 | 1.0636 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 2
181482 CHD120 120.00 | 1.0887 | 1.0641 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
181501 BH120A 120.00 | 1.1263 | 1.0789 | T:MMS1&2 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147837 [MASS230A 230.00] CKT 1 TRIP BRANCH FROM BUS 147839 [MOSES E 230.00] TO BUS 147838 [MASS230B 230.00] CKT 1
181506 CED120 120.00 | 0.9345 | 0.9792 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180475 [LGL315 315.00] CKT 1
181509 B120CD 120.00 | 0.9374 | 0.9809 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180475 [LGL315 315.00] CKT 1
181552 RA2120 120.00 | 1.0502 | 1.0497 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
181553 RA7120 120.00 | 1.051 | 1.0505 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
181554 R15120 120.00 | 1.0637 | 1.0636 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 2
181556 PRC120 120.00 | 1.0515 | 1.0504 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 2
181620 ROMAINE_1 161.00 | 0.8982 | 0.9531 | OPEN LINE FROM BUS 180411 [ROM1-315B 315.00] TO BUS 181620 [ROMAINE_1 161.00] CKT 1
181621 D-ROMAINE 161.00 | 0.8988 | 0.9503 | OPEN LINE FROM BUS 180411 [ROM1-315B 315.00] TO BUS 181620 [ROMAINE_1 161.00] CKT 1
182003 LEV230 230.00 | 1.0504 | 1.0247 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
182071 RCOEUR A230.00 | 1.0509 | 1.0494 | OPEN LINE FROM BUS 180488 [MAURIC 315.00] TO BUS 183625 [AGBOIS 315.00] CKT 1
182081 CHALLAR A230.00 | 1.0526 | 1.0514 | OPEN LINE FROM BUS 180488 [MAURIC 315.00] TO BUS 183625 [AGBOIS 315.00] CKT 1
182086 SHR230 230.00 | 0.9083 | 0.9523 | OPEN LINE FROM BUS 182055 [CAN230 230.00] TO BUS 182086 [SHR230 230.00] CKT 1
182087 SHR230 A230.00 | 0.9259 | 0.9482 | OPEN LINE FROM BUS 182088 [SHR230 B230.00] TO BUS 181189 [SHR120 120.00] CKT 3
182088 SHR230 B230.00 | 0.9254 | 0.9482 | OPEN LINE FROM BUS 182087 [SHR230 A230.00] TO BUS 181189 [SHR120 120.00] CKT 2
182143 PAU230 230.00 | 1.0723 | 1.0706 | OPEN LINE FROM BUS 180458 [VGN315 315.00] TO BUS 181258 [VGN120 120.00] CKT 4
182199 MNY230 A230.00 | 0.9234 | 1.0065 | OPEN LINE FROM BUS 186273 [BOURD1 230.00] TO BUS 186287 [DURAD1 230.00] CKT 1
182222 LAT230 230.00 | 1.0519 | 1.0393 | OPEN LINE FROM BUS 182222 [LAT230 230.00] TO BUS 182835 [TUQ230 230.00] CKT 1
182292 BOC230 230.00 | 1.0515 | 1.0357 | OPEN LINE FROM BUS 182292 [BOC230 230.00] TO BUS 185895 [ANTLEM 230.00] CKT 1
182298 QUY230 230.00 | 1.069 | 1.0521 | OPEN LINE FROM BUS 182348 [CDC230 230.00] TO BUS 180048 [CDCHAT 13.800] CKT 1
182348 CDC230 230.00 | 1.0691 | 1.0516 | OPEN LINE FROM BUS 182348 [CDC230 230.00] TO BUS 180048 [CDCHAT 13.800] CKT 1
182359 CHU230 230.00 | 1.0537 | 1.0522 | OPEN LINE FROM BUS 180412 [MUR315 315.00] TO BUS 180122 [ROM2-BT 18.000] CKT 1
182360 CHUR-22 230.00 | 1.0557 | 1.0539 | OPEN LINE FROM BUS 180412 [MUR315 315.00] TO BUS 180122 [ROM2-BT 18.000] CKT 1
182700 BLAISD 120.00 | 1.0703 | 1.0697 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
182720 SNTERE 120.00 | 1.0789 | 1.0783 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
182725 SEN120 120.00 | 1.0797 | 1.0791 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
182749 DQUEVI 120.00 | 1.0705 | 1.0549 | OPEN LINE FROM BUS 180528 [LBL315 315.00] TO BUS 181128 [LBL120 120.00] CKT 1
183026 CHENAU A230.00 | 0.8485 | 0.9817 | OPEN LINE FROM BUS 182274 [DCH-D2 230.00] TO BUS 183026 [CHENAU A230.00] CKT 1
183153 D-SHELDRAKE 161.00 | 0.8982 | 0.9402 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
183154 SHELD 161.00 | 0.8974 | 0.9394 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
183384 D-ALOUE3 161.00 | 0.9456 | 0.9833 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183385 ALOUET 161.00 | 0.9456 | 0.9833 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183387 ALOUE2 161.00 | 0.9456 | 0.9833 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183424 DRTONE 161.00 | 0.8955 | 0.9364 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
183425 RTONER 161.00 | 0.905 | 0.9364 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183426 SECT65-19 161.00 | 0.905 | 0.9364 | OPEN LINE FROM BUS 180309 [ARN315 315.00] TO BUS 180409 [ARN315 A315.00] CKT 1
183435 HAVRE 161.00 | 0.899 | 0.9256 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
183474 DER_MAGPIE 161.00 | 0.8948 | 0.9329 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
183475 MAGPIE 161.00 | 0.8949 | 0.9329 | OPEN LINE FROM BUS 180409 [ARN315 A315.00] TO BUS 180709 [ARN735 735.00] CKT 2
183620 CHATEL 315.00 | 0.941 | 1.0129 | OPEN LINE FROM BUS 180304 [LTD315 315.00] TO BUS 183620 [CHATEL 315.00] CKT 1
183625 AGBOIS 315.00 | 1.0752 | 1.0416 | OPEN LINE FROM BUS 183625 [AGBOIS 315.00] TO BUS 183627 [DESCHA 315.00] CKT 1
183627 DESCHA 315.00 | 1.0589 | 1.0356 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
184026 DALMA 230.00 | 1.0551 | 1.0176 | OPEN LINE FROM BUS 182132 [IM230 230.00] TO BUS 184026 [DALMA 230.00] CKT 1
184111 GBAIE2 161.00 | 0.9232 | 0.9313 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
184112 GBAIE1 161.00 | 0.9232 | 0.9313 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
184165 MANIWA 120.00 | 1.0524 | 1.0516 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
184260 LDILES 120.00 | 1.074 | 1.0617 | OPEN LINE FROM BUS 180770 [BRU735 735.00] TO BUS 181170 [BRU120 120.00] CKT 1
184275 MLRIER120A 120.00 | 1.0811 | 1.0689 | OPEN LINE FROM BUS 180770 [BRU735 735.00] TO BUS 181170 [BRU120 120.00] CKT 1
184280 NDLAUS 120.00 | 1.0675 | 1.055 | OPEN LINE FROM BUS 180770 [BRU735 735.00] TO BUS 181170 [BRU120 120.00] CKT 1
184500 VALLEY 120.00 | 0.9213 | 0.9703 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184505 MGREMA 120.00 | 0.9236 | 0.9725 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184508 V-SOULB1 120.00 | 0.923 | 0.9711 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184514 EKADER 120.00 | 0.9221 | 0.9709 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184515 LAROCQ 120.00 | 0.9225 | 0.9713 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184521 RIVSUD315-1 315.00 | 1.0762 | 1.0002 | OPEN LINE FROM BUS 184519 [RIVSUD-D1 315.00] TO BUS 184521 [RIVSUD315-1 315.00] CKT 1
184522 RIVSUD315-2 315.00 | 1.0763 | 1.0002 | OPEN LINE FROM BUS 184520 [RIVSUD-D2 315.00] TO BUS 184522 [RIVSUD315-2 315.00] CKT 1
184579 D-ERIC1 120.00 | 0.9238 | 0.9719 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184580 D-ERIC2 120.00 | 0.9237 | 0.9716 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184590 NAPIER 120.00 | 0.9413 | 0.9526 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180419 [CHATG 315.00] CKT 1
184653 BRO315 A315.00 | 0.9483 | 0.9953 | OPEN LINE FROM BUS 184650 [BRO315 315.00] TO BUS 184646 [BROSB61 26.400] CKT 1
184670 DUTREMBL_B1 315.00 | 0.8604 | 1.0029 | OPEN LINE FROM BUS 180301 [BCV315 315.00] TO BUS 184678 [D-TREMBLAY-1315.00] CKT 1
184671 DUTREMBL_B4 315.00 | 0.8709 | 1.0029 | OPEN LINE FROM BUS 184671 [DUTREMBL_B4 315.00] TO BUS 184679 [D-TREMBLAY-2315.00] CKT 1
184678 D-TREMBLAY-1315.00 | 0.8604 | 1.0033 | OPEN LINE FROM BUS 180301 [BCV315 315.00] TO BUS 184678 [D-TREMBLAY-1315.00] CKT 1
184679 D-TREMBLAY-2315.00 | 0.8739 | 1.0034 | OPEN LINE FROM BUS 180301 [BCV315 315.00] TO BUS 184679 [D-TREMBLAY-2315.00] CKT 1
184844 DGYEAR 120.00 | 0.9231 | 0.972 | OPEN LINE FROM BUS 180319 [CHA315 315.00] TO BUS 180476 [LGL315 A315.00] CKT 1
184850 D-ARCELMITTL315.00 | 0.8604 | 1.0033 | OPEN LINE FROM BUS 180301 [BCV315 315.00] TO BUS 184678 [D-TREMBLAY-1315.00] CKT 1
185035 YAMASK 120.00 | 0.9449 | 0.9634 | OPEN LINE FROM BUS 182007 [NIC230 230.00] TO BUS 182279 [RIO230 A230.00] CKT 1
185329 DMAGOG 120.00 | 0.9373 | 0.9772 | OPEN LINE FROM BUS 182055 [CAN230 230.00] TO BUS 182087 [SHR230 A230.00] CKT 1
185330 MAGOG 120.00 | 0.9371 | 0.9771 | OPEN LINE FROM BUS 182055 [CAN230 230.00] TO BUS 182087 [SHR230 A230.00] CKT 1
185463 HMAGDR 120.00 | 0.9378 | 0.9777 | OPEN LINE FROM BUS 182055 [CAN230 230.00] TO BUS 182087 [SHR230 A230.00] CKT 1
185466 DEAG1 120.00 | 0.9454 | 0.9918 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
185476 DWEED 120.00 | 0.9432 | 0.9911 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
185780 CLAIRE 120.00 | 0.9332 | 1.0153 | OPEN LINE FROM BUS 182282 [CHD230 230.00] TO BUS 181482 [CHD120 120.00] CKT 1
185955 WEEDON 120.00 | 0.9086 | 0.9842 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
185965 COLERA 120.00 | 0.8462 | 1.0186 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
185970 LAMTON 120.00 | 0.9011 | 0.9888 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
185972 LAMDER 120.00 | 0.8904 | 0.987 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
185975 MEGANT 120.00 | 0.8641 | 0.9839 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
185985 EVARIS 120.00 | 0.9248 | 0.9927 | OPEN LINE FROM BUS 182290 [THE230 230.00] TO BUS 181390 [THE120 120.00] CKT 1
186266 LEVIS 230.00 | 1.0502 | 1.0244 | OPEN LINE FROM BUS 180626 [CDP345 345.00] TO BUS 180026 [PASSES 14.400] CKT 1
186287 DURAD1 230.00 | 0.9223 | 1.0144 | OPEN LINE FROM BUS 186273 [BOURD1 230.00] TO BUS 186287 [DURAD1 230.00] CKT 1
186288 DURAD2 230.00 | 0.9208 | 1.0144 | OPEN LINE FROM BUS 186275 [BOURD2 230.00] TO BUS 186288 [DURAD2 230.00] CKT 1
186390 CACOUN 120.00 | 1.0562 | 1.0273 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186407 SOUCYD 120.00 | 1.0531 | 1.0225 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186410 ANSEVA 161.00 | 1.082 | 1.0769 | OPEN LINE FROM BUS 182174 [MTP230 230.00] TO BUS 186946 [DCARLE 230.00] CKT 1
186411 DANSEV 161.00 | 1.0819 | 1.0768 | OPEN LINE FROM BUS 182174 [MTP230 230.00] TO BUS 186946 [DCARLE 230.00] CKT 1
186430 LACALF1-315E315.00 | 1.0822 | 1.0728 | OPEN LINE FROM BUS 186430 [LACALF1-315E315.00] TO BUS 186437 [LACALF3--35E34.500] CKT 1
186431 LACALF1-315D315.00 | 1.0857 | 1.0739 | OPEN LINE FROM BUS 186430 [LACALF1-315E315.00] TO BUS 186431 [LACALF1-315D315.00] CKT 1
186460 LEPLAT1-315E315.00 | 1.0878 | 1.0729 | OPEN LINE FROM BUS 186460 [LEPLAT1-315E315.00] TO BUS 186462 [LEPLAT1--35E34.500] CKT 1
186461 LEPLAT1-315D315.00 | 1.0878 | 1.0728 | OPEN LINE FROM BUS 186460 [LEPLAT1-315E315.00] TO BUS 186462 [LEPLAT1--35E34.500] CKT 1
186481 S1451 120.00 | 1.053 | 1.0264 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186484 SULLYD 120.00 | 1.053 | 1.0264 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186504 FFSOUD 120.00 | 1.0529 | 1.0222 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186505 GRDPOR 120.00 | 1.0529 | 1.0222 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186540 TEMISC1-120E120.00 | 1.0528 | 1.0266 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186541 TEMISC1-120D120.00 | 1.0528 | 1.0266 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186580 VIGDEN1-120E120.00 | 1.0565 | 1.03 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186581 VIGDEN1-120D120.00 | 1.0565 | 1.03 | OPEN LINE FROM BUS 180472 [RDL315 315.00] TO BUS 181272 [RDL120 120.00] CKT 3
186777 DANSP 230.00 | 1.0864 | 1.08 | OPEN LINE FROM BUS 190420 [STANDR 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
186790 RENARD 161.00 | 1.0619 | 1.0554 | OPEN LINE FROM BUS 182174 [MTP230 230.00] TO BUS 186946 [DCARLE 230.00] CKT 1
186970 MTLOUI 230.00 | 1.082 | 1.075 | OPEN LINE FROM BUS 180675 [MADAWA A345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
186975 GROSMO 230.00 | 1.0893 | 1.0833 | OPEN LINE FROM BUS 190420 [STANDR 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
186976 DMTLOUIS 230.00 | 1.082 | 1.075 | OPEN LINE FROM BUS 190420 [STANDR 345.00] TO BUS 190619 [EDMN345 345.00] CKT 1
186980 MONTSE 161.00 | 1.0938 | 1.0895 | OPEN LINE FROM BUS 182174 [MTP230 230.00] TO BUS 186946 [DCARLE 230.00] CKT 1
187005 BOURSA 120.00 | 1.0987 | 1.0205 | OPEN LINE FROM BUS 180428 [BDL315 315.00] TO BUS 181228 [BDL120 120.00] CKT 8
187010 MTL-E 120.00 | 1.0951 | 1.0169 | OPEN LINE FROM BUS 180428 [BDL315 315.00] TO BUS 181228 [BDL120 120.00] CKT 8
187030 LONGPT 120.00 | 1.0729 | 1.0384 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187035 DELORM 120.00 | 1.0726 | 1.0377 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187040 JEANNE 120.00 | 1.0726 | 1.0379 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187045 BERRI 120.00 | 1.0712 | 1.0363 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187201 LANGE1 315.00 | 1.0771 | 1.0455 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187202 LANGE2 315.00 | 1.077 | 1.0454 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187203 DLANG1 315.00 | 1.0771 | 1.0455 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187204 DLANG2 315.00 | 1.077 | 1.0454 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187209 MTLEST A315.00 | 0.9289 | 1.0114 | OPEN LINE FROM BUS 187206 [MTLESD 315.00] TO BUS 187209 [MTLEST A315.00] CKT 1
187279 SOURC315-1 315.00 | 1.0634 | 1.0315 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187280 SOURC315-2 315.00 | 1.0634 | 1.0314 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187281 DSOUR1 315.00 | 1.0648 | 1.0331 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187282 DSOUR2 315.00 | 1.0648 | 1.0331 | OPEN LINE FROM BUS 180302 [DUV315 315.00] TO BUS 180702 [DUV735 735.00] CKT 3
187328 DELOR315-2 315.00 | 1.0649 | 1.0098 | OPEN LINE FROM BUS 180463 [VIG315 315.00] TO BUS 187328 [DELOR315-2 315.00] CKT 1
188225 DORION 120.00 | 0.9256 | 0.9722 | OPEN LINE FROM BUS 180475 [LGL315 315.00] TO BUS 181275 [LGL120 120.00] CKT 2
188630 ALPHA 120.00 | 1.0537 | 1.029 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
188631 DALPH1 120.00 | 1.0539 | 1.0292 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
188632 DALPH2 120.00 | 1.0539 | 1.0292 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
188795 JOLIET 120.00 | 1.0539 | 1.0292 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
189178 HET<A> 230.00 | 1.055 | 1.041 | OPEN LINE FROM BUS 180317 [JCA315 315.00] TO BUS 180717 [JCA735 735.00] CKT 2
190006 EELRVR 138.00 | 1.0569 | 1.0242 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190008 DALTOWN 138.00 | 1.0551 | 1.0223 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190072 IROQT1 138.00 | 1.0873 | 1.0209 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190084 EELRVR 230.00 | 1.0719 | 1.0373 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190111 LOCLOM 138.00 | 0.9343 | 0.9887 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190179 11401214 138.00 | 1.0875 | 1.021 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190199 SALBRY 230.00 | 1.0642 | 0.9843 | OPEN LINE FROM BUS 190199 [SALBRY 230.00] TO BUS 190200 [SALBRY 138.00] CKT 1
190237 BR3016 345.00 | 1.0636 | 1.0389 | OPEN LINE FROM BUS 190231 [LEPRAU 345.00] TO BUS 190237 [BR3016 345.00] CKT 1
190246 LAKEWD 138.00 | 0.9479 | 0.9948 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190251 BUCTCW 138.00 | 0.9326 | 0.9743 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190252 RICHBT 138.00 | 0.9417 | 0.9829 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190260 114963 138.00 | 0.9355 | 0.9924 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190278 114908 138.00 | 0.9364 | 0.9907 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190290 114987 138.00 | 0.9364 | 0.9907 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190310 STANDR 138.00 | 1.0553 | 1.0252 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190343 HAMPTN 138.00 | 0.9419 | 1.0011 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190354 STLOUS 138.00 | 0.9462 | 0.9871 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190357 T1140L17 138.00 | 1.085 | 1.018 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190362 MCCNGF 138.00 | 1.0846 | 1.0175 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190370 ELLIOTRD 138.00 | 0.9352 | 0.9921 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190374 GONDPT 138.00 | 0.9322 | 0.9892 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190405 AVCELL 138.00 | 1.0563 | 1.0236 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190406 111036 138.00 | 1.0567 | 1.024 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190410 EDMSTN 138.00 | 1.0891 | 1.0227 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190411 IROQT2 138.00 | 1.0848 | 1.0187 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190418 T1149HPT 138.00 | 0.9423 | 1.0016 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190419 EDMSTN 345.00 | 1.1276 | 1.0586 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190420 STANDR 345.00 | 1.0978 | 1.0529 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190426 114084 138.00 | 1.0876 | 1.0211 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190437 FAIRVALE 138.00 | 0.9348 | 0.9892 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190447 T1110QTN 138.00 | 1.0536 | 1.0216 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190448 STQNTN 138.00 | 1.0531 | 1.0212 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190475 FRSEDM 138.00 | 1.0818 | 1.0158 | HQ_SYNC_DC OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190479 STBASI 138.00 | 1.0875 | 1.021 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2
190492 REXTON 138.00 | 0.9393 | 0.9806 | OPEN LINE FROM BUS 190197 [C.COVE 345.00] TO BUS 190498 [NORTON 345.00] CKT 1
190619 EDMN345 345.00 | 1.1276 | 1.0586 | HQ_SYNC_DC&OMS TRIP BRANCH FROM BUS 107410 [SANDBAR REAC115.00] TO BUS 107400 [SANDBAR 115.00] CKT 2 OPEN LINE FROM BUS 107326 [HG_CONVRTR_N120.00] TO BUS 107330 [HIGHGATE_HQ 120.00] CKT 1OPEN LINE FROM BUS 107324 [HG_CONVRTR_S115.00] TO BUS 107310 [HIGHGATE_TAP115.00] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190491 [EELSC1 13.000] CKT 1OPEN LINE FROM BUS 190490 [EEL34A 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190494 [EELDC2NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190507 [EELSC2 13.000] CKT 1OPEN LINE FROM BUS 190497 [EEL34BY 34.500] TO BUS 190496 [EEL230 230.00] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190495 [EELSC3 13.000] CKT 1OPEN LINE FROM BUS 190493 [EELDC1NB 34.500] TO BUS 190084 [EELRVR 230.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 1OPEN LINE FROM BUS 180575 [MADAWA 315.00] TO BUS 180472 [RDL315 315.00] CKT 2

## MISO_N-1_VOLTAGE_WINTER
BUS | VCONT | VINIT | CONTINGENCY | COMMENTS
249835 08SCTBRG 138.00 | 0.9323 | 0.962 | OPEN LINE FROM BUS 249628 [08PUMPCT 230.00] TO BUS 250762 [08PMKN C 69.000] CKT 1
264658 19SANDU 120.00 | 0.8601 | 1.0453 | OPEN LINE FROM BUS 265077 [19BANNER 345.00] TO BUS 265088 [19BANNER 120.00] CKT 1
264753 19BUNCE 220.00 | 1.0606 | 1.0598 | OPEN LINE FROM BUS 264753 [19BUNCE 220.00] TO BUS 264883 [19B3N PS 220.00] CKT 1 | Connected to IESO system, IESO planning criteria should be applied.
264830 19STCPP 220.00 | 1.0692 | 1.0685 | OPEN LINE FROM BUS 264830 [19STCPP 220.00] TO BUS 160065 [LAMBTON_L51D220.00] CKT 1 | Connected to IESO system, IESO planning criteria should be applied.
264883 19B3N PS 220.00 | 1.0606 | 1.0595 | OPEN LINE FROM BUS 264883 [19B3N PS 220.00] TO BUS 160063 [SCOTT_TS 220.00] CKT 1 | Connected to IESO system, IESO planning criteria should be applied.
265088 19BANNER 120.00 | 0.8601 | 1.0464 | OPEN LINE FROM BUS 265077 [19BANNER 345.00] TO BUS 265088 [19BANNER 120.00] CKT 1
303101 6MOSS_BLUFF!230.00 | 0.939 | 0.9971 | OPEN LINE FROM BUS 303101 [6MOSS_BLUFF!230.00] TO BUS 335190 [6NELSON% 230.00] CKT 1
303102 6CHALKLEY! 230.00 | 0.9394 | 0.972 | OPEN LINE FROM BUS 335190 [6NELSON% 230.00] TO BUS 335206 [1NELSON_G6! 20.000] CKT 1
318021 6BENDL230 230.00 | 0.926 | 0.9756 | OPEN LINE FROM BUS 318021 [6BENDL230 230.00] TO BUS 318261 [6SE.GREEN 230.00] CKT 1
318261 6SE.GREEN 230.00 | 0.9153 | 0.981 | OPEN LINE FROM BUS 318261 [6SE.GREEN 230.00] TO BUS 317009 [6MC SW230 230.00] CKT 1
318263 5SE.GREEN 161.00 | 0.917 | 0.9916 | OPEN LINE FROM BUS 318261 [6SE.GREEN 230.00] TO BUS 317009 [6MC SW230 230.00] CKT 1
334436 6P AC BK% 230.00 | 0.9319 | 0.9674 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334437 6KOLBS% 230.00 | 0.9235 | 0.9702 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334438 6HANKS 230.00 | 0.9234 | 0.9725 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334444 6KEITHLAKE% 230.00 | 0.93 | 0.9656 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334445 6SOSIDE! 230.00 | 0.9309 | 0.9665 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334446 6SLTGRAS! 230.00 | 0.9312 | 0.9668 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
334447 6VALSOUTH! 230.00 | 0.9312 | 0.9667 | OPEN LINE FROM BUS 334438 [6HANKS 230.00] TO BUS 334442 [6GULFWAY% 230.00] CKT 1
335078 6VINCENT 230.00 | 0.9347 | 0.9653 | OPEN LINE FROM BUS 335190 [6NELSON% 230.00] TO BUS 335206 [1NELSON_G6! 20.000] CKT 1
335079 6GRAYWOOD% 230.00 | 0.9308 | 0.9617 | OPEN LINE FROM BUS 335190 [6NELSON% 230.00] TO BUS 335206 [1NELSON_G6! 20.000] CKT 1
335080 6GRAYWOOD_TP230.00 | 0.9301 | 0.9616 | OPEN LINE FROM BUS 335190 [6NELSON% 230.00] TO BUS 335206 [1NELSON_G6! 20.000] CKT 1
335134 6MICHIGAN% 230.00 | 0.927 | 0.9978 | OPEN LINE FROM BUS 335134 [6MICHIGAN% 230.00] TO BUS 335190 [6NELSON% 230.00] CKT 1
335135 6VERDINE% 230.00 | 0.9289 | 0.9918 | OPEN LINE FROM BUS 335134 [6MICHIGAN% 230.00] TO BUS 335190 [6NELSON% 230.00] CKT 1
335136 6PPG! 230.00 | 0.9331 | 0.9836 | OPEN LINE FROM BUS 335134 [6MICHIGAN% 230.00] TO BUS 335190 [6NELSON% 230.00] CKT 1
335189 8LOFCAR 500.00 | 0.9329 | 0.9863 | OPEN LINE FROM BUS 335188 [8SULPHUR_LN%500.00] TO BUS 335189 [8LOFCAR 500.00] CKT 1
335244 6SOLAC! 230.00 | 0.9297 | 0.9615 | OPEN LINE FROM BUS 335190 [6NELSON% 230.00] TO BUS 335206 [1NELSON_G6! 20.000] CKT 1
336003 6DNLDVL 230.00 | 0.9235 | 0.9802 | OPEN LINE FROM BUS 336001 [6EVGREN! 230.00] TO BUS 336003 [6DNLDVL 230.00] CKT 1
336004 6BYVRET! 230.00 | 0.9238 | 0.9752 | OPEN LINE FROM BUS 336001 [6EVGREN! 230.00] TO BUS 336003 [6DNLDVL 230.00] CKT 1
336005 6WELCOM! 230.00 | 0.9281 | 0.9751 | OPEN LINE FROM BUS 336001 [6EVGREN! 230.00] TO BUS 336003 [6DNLDVL 230.00] CKT 1
336006 6STJAME! 230.00 | 0.936 | 0.9781 | OPEN LINE FROM BUS 336006 [6STJAME! 230.00] TO BUS 336007 [6VACHRE! 230.00] CKT 1
338995 6NSUB2% 230.00 | 0.9366 | 0.9811 | OPEN LINE FROM BUS 335134 [6MICHIGAN% 230.00] TO BUS 335190 [6NELSON% 230.00] CKT 1
338996 6NSUB1% 230.00 | 0.9332 | 0.9829 | OPEN LINE FROM BUS 335134 [6MICHIGAN% 230.00] TO BUS 335190 [6NELSON% 230.00] CKT 1
348285 6STJOHNAM 230.00 | 0.9067 | 1.0232 | OPEN LINE FROM BUS 348285 [6STJOHNAM 230.00] TO BUS 348286 [6STJOHN TAP 230.00] CKT Z
502417 ELKS 6 230.00 | 0.9034 | 0.9906 | OPEN LINE FROM BUS 502417 [ELKS 6 230.00] TO BUS 502425 [BEADLE 6 230.00] CKT 1
502425 BEADLE 6 230.00 | 0.9234 | 0.9918 | OPEN LINE FROM BUS 502401 [FLANDER6 230.00] TO BUS 502425 [BEADLE 6 230.00] CKT 1
601001 FORBES 2 500.00 | 1.0715 | 1.0342 | OPEN LINE FROM BUS 601016 [CHIS CO2 500.00] TO BUS 601017 [CHIS-N 2 500.00] CKT 1
601012 ROSEAUN2 500.00 | 1.1373 | 1.0985 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
601013 ROSEAUS2 500.00 | 1.1373 | 1.0632 | OPEN LINE FROM BUS 601013 [ROSEAUS2 500.00] TO BUS 601038 [ROSEAUM 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
601017 CHIS-N 2 500.00 | 1.1164 | 0.9896 | OPEN LINE FROM BUS 601016 [CHIS CO2 500.00] TO BUS 601017 [CHIS-N 2 500.00] CKT 1
601038 ROSEAUM 2 500.00 | 1.1373 | 1.0787 | OPEN LINE FROM BUS 601012 [ROSEAUN2 500.00] TO BUS 667501 [RIEL 2 500.00] CKT 1 | SPS mitigates outages on this line - during contingency conditions. For basecase - Higher voltage thresholds for this line
603007 PRASWCP7 115.00 | 1.0764 | 1.0631 | OPEN LINE FROM BUS 657755 [PRAIRIE4 230.00] TO BUS 657712 [PRAIRIE7 115.00] TO BUS 605746 [PRA TR7 9 13.800] CKT 3
603218 SHEAS LK 7 115.00 | 0.888 | 1.0276 | OPEN LINE FROM BUS 601072 [SHEAS LK3 345.00] TO BUS 603218 [SHEAS LK 7 115.00] TO BUS 605756 [SHEAS LK9 34.500] CKT 9
608410 WARRVRN2 500.00 | 1.1193 | 1.1175 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667500 [DORSEY 2 500.00] TO BUS 669102 [DORSEYT9 46.000] CKT 52
615665 GRE-RIVRVRD7115.00 | 0.9167 | 1.046 | OPEN LINE FROM BUS 615664 [GRE-RIVRVRD3345.00] TO BUS 615665 [GRE-RIVRVRD7115.00] TO BUS 615666 [GRE-RIVRRD1T34.500] CKT 1
620214 BIGSTON7 115.00 | 1.063 | 1.0384 | OPEN LINE FROM BUS 620314 [BIGSTON4 230.00] TO BUS 620315 [BIGSTN1G 24.000] CKT 1
620215 HIWY12 7 115.00 | 1.0618 | 1.0381 | OPEN LINE FROM BUS 620314 [BIGSTON4 230.00] TO BUS 620315 [BIGSTN1G 24.000] CKT 1
620861 TRF_230 230.00 | 0.9366 | 1.0039 | OPEN LINE FROM BUS 620861 [TRF_230 230.00] TO BUS 657758 [WINGER 4 230.00] CKT 1
652422 HALIDAY7 115.00 | 0.9483 | 1.0089 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
652423 BARLOW 7 115.00 | 0.9474 | 0.9975 | OPEN LINE FROM BUS 615335 [GRE-RAMSEY 4230.00] TO BUS 620266 [RAMSEY 7 115.00] TO BUS 615337 [GRE-RAMSEY T12.470] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
652448 LAKOTA 7 115.00 | 0.9362 | 1.0038 | OPEN LINE FROM BUS 615335 [GRE-RAMSEY 4230.00] TO BUS 620266 [RAMSEY 7 115.00] TO BUS 615337 [GRE-RAMSEY T12.470] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
657717 ULRICH 7 115.00 | 0.9464 | 1.0173 | OPEN LINE FROM BUS 620336 [AUDUBON4 230.00] TO BUS 658112 [AUDUBON7 115.00] TO BUS 658113 [AUDUBON9 41.600] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
657719 MORANVI7 115.00 | 0.9116 | 0.9536 | OPEN LINE FROM BUS 602012 [ROSSWCP4 230.00] TO BUS 602013 [ROSEAU 4 230.00] CKT Z | WAPA violation: MISO doesn't have a topology update to provide.
658060 DLWEST 7 115.00 | 0.9465 | 1.0192 | OPEN LINE FROM BUS 620336 [AUDUBON4 230.00] TO BUS 658112 [AUDUBON7 115.00] TO BUS 658113 [AUDUBON9 41.600] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
658062 DLINDUST 115.00 | 0.9446 | 1.0153 | OPEN LINE FROM BUS 620336 [AUDUBON4 230.00] TO BUS 658112 [AUDUBON7 115.00] TO BUS 658113 [AUDUBON9 41.600] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
658064 DLFRONTST7 115.00 | 0.9444 | 1.0151 | OPEN LINE FROM BUS 620336 [AUDUBON4 230.00] TO BUS 658112 [AUDUBON7 115.00] TO BUS 658113 [AUDUBON9 41.600] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
658112 AUDUBON7 115.00 | 0.9482 | 1.0254 | OPEN LINE FROM BUS 620336 [AUDUBON4 230.00] TO BUS 658112 [AUDUBON7 115.00] TO BUS 658113 [AUDUBON9 41.600] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
658202 DLWEST CAP 7115.00 | 0.9465 | 1.0192 | OPEN LINE FROM BUS 620336 [AUDUBON4 230.00] TO BUS 658112 [AUDUBON7 115.00] TO BUS 658113 [AUDUBON9 41.600] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659205 BRDLAND4 230.00 | 1.0609 | 1.014 | OPEN LINE FROM BUS 652514 [HURON 4 230.00] TO BUS 659205 [BRDLAND4 230.00] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659271 RCDC EAST 4230.00 | 1.0715 | 1.025 | OPEN LINE FROM BUS 652484 [NUNDRWD4 230.00] TO BUS 659271 [RCDC EAST 4230.00] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659363 WHEELOCK 7115.00 | 0.9098 | 0.991 | OPEN LINE FROM BUS 659362 [WHEELOCK 4230.00] TO BUS 659363 [WHEELOCK 7115.00] TO BUS 659364 [WHEELOCK 913.800] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659416 BEPCPKFT 7115.00 | 0.9232 | 0.9827 | OPEN LINE FROM BUS 659362 [WHEELOCK 4230.00] TO BUS 659363 [WHEELOCK 7115.00] TO BUS 659364 [WHEELOCK 913.800] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659420 ANTELOP-LNX3345.00 | 1.0852 | 1.0203 | OPEN LINE FROM BUS 659101 [ANTELOP3 345.00] TO BUS 659420 [ANTELOP-LNX3345.00] CKT Z | WAPA violation: MISO doesn't have a topology update to provide.
659421 BRDLAND-LNX3345.00 | 1.0613 | 1.0197 | OPEN LINE FROM BUS 659120 [BRDLAND3 345.00] TO BUS 659421 [BRDLAND-LNX3345.00] CKT Z | WAPA violation: MISO doesn't have a topology update to provide.
659424 LELAND2-LNX3345.00 | 1.0916 | 1.0223 | OPEN LINE FROM BUS 659105 [LELANDO3 345.00] TO BUS 659424 [LELAND2-LNX3345.00] CKT Z | WAPA violation: MISO doesn't have a topology update to provide.
659579 SPRNGBRK-MW7115.00 | 0.9145 | 0.9859 | OPEN LINE FROM BUS 659362 [WHEELOCK 4230.00] TO BUS 659363 [WHEELOCK 7115.00] TO BUS 659364 [WHEELOCK 913.800] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659638 SEWLLSTN-MW7115.00 | 0.9325 | 0.9839 | OPEN LINE FROM BUS 659362 [WHEELOCK 4230.00] TO BUS 659363 [WHEELOCK 7115.00] TO BUS 659364 [WHEELOCK 913.800] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
659639 TWELVEMILMW7115.00 | 0.9232 | 0.9827 | OPEN LINE FROM BUS 659362 [WHEELOCK 4230.00] TO BUS 659363 [WHEELOCK 7115.00] TO BUS 659364 [WHEELOCK 913.800] CKT 1 | WAPA violation: MISO doesn't have a topology update to provide.
661008 BEULAH 7 115.00 | 0.9327 | 1.014 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661018 COYOTE 7 115.00 | 0.9424 | 1.015 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661019 MATHSON7 115.00 | 0.9303 | 0.9918 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661020 DIXGREENRVR7115.00 | 0.9212 | 0.9919 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661021 WSTMD1 7 115.00 | 0.9335 | 1.0132 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661022 DICKNTH7 115.00 | 0.9203 | 0.9861 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661024 WDICKSN7 115.00 | 0.9232 | 0.9867 | OPEN LINE FROM BUS 657791 [CENTER 3 345.00] TO BUS 661016 [COYOTE 3 345.00] CKT 1 | Coveredy by Coyote Continuity SPS
661037 BOWDLE 7 115.00 | 0.9353 | 0.9632 | OPEN LINE FROM BUS 661038 [GLENHAM4 230.00] TO BUS 661035 [GLENHAM7 115.00] TO BUS 661600 [GLENHAM9 41.600] CKT 2
661039 MOBRIDG7 115.00 | 0.9387 | 0.9666 | OPEN LINE FROM BUS 661038 [GLENHAM4 230.00] TO BUS 661035 [GLENHAM7 115.00] TO BUS 661600 [GLENHAM9 41.600] CKT 2
661040 MCLGHLN7 115.00 | 0.9211 | 0.9498 | OPEN LINE FROM BUS 661038 [GLENHAM4 230.00] TO BUS 661035 [GLENHAM7 115.00] TO BUS 661600 [GLENHAM9 41.600] CKT 2
661041 MCINTSH7 115.00 | 0.9213 | 0.9502 | OPEN LINE FROM BUS 661038 [GLENHAM4 230.00] TO BUS 661035 [GLENHAM7 115.00] TO BUS 661600 [GLENHAM9 41.600] CKT 2
667056 CRANBTP4 230.00 | 0.9455 | 1.0059 | OPEN LINE FROM BUS 667054 [HERB LK4 230.00] TO BUS 667055 [CLIFFLK4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667064 RAVLAKE4 230.00 | 0.9357 | 0.9911 | OPEN LINE FROM BUS 667062 [VERMIL 4 230.00] TO BUS 667064 [RAVLAKE4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667065 BIRTLE 4 230.00 | 0.9272 | 0.9915 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667066 VIRDN W4 230.00 | 0.9111 | 0.9926 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667067 RESTON 4 230.00 | 0.9055 | 0.9983 | OPEN LINE FROM BUS 672601 [BD 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667072 WHTSL2 4 220.00 | 1.1256 | 1.1029 | OPEN LINE FROM BUS 667072 [WHTSL2 4 220.00] TO BUS 668092 [WHSL2PH7 110.00] CKT 8 | MH violation: MISO doesn't have an update to provide.
667073 WHTSL1 4 220.00 | 1.1256 | 1.1029 | OPEN LINE FROM BUS 667073 [WHTSL1 4 220.00] TO BUS 668091 [WHSL1PH7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
667214 OXFORD 6 138.00 | 0.8811 | 0.8912 | OPEN LINE FROM BUS 667017 [KELSEY 4 230.00] TO BUS 667217 [KELSEY 6 138.00] CKT 10 | MH violation: MISO doesn't have an update to provide.
667215 GODSNAR6 138.00 | 0.8332 | 0.844 | OPEN LINE FROM BUS 667017 [KELSEY 4 230.00] TO BUS 667217 [KELSEY 6 138.00] CKT 10 | MH violation: MISO doesn't have an update to provide.
667219 WASAGMK6 138.00 | 0.7861 | 0.7977 | OPEN LINE FROM BUS 667017 [KELSEY 4 230.00] TO BUS 667217 [KELSEY 6 138.00] CKT 10 | MH violation: MISO doesn't have an update to provide.
667221 GARDNHL6 138.00 | 0.7944 | 0.8059 | OPEN LINE FROM BUS 667017 [KELSEY 4 230.00] TO BUS 667217 [KELSEY 6 138.00] CKT 10 | MH violation: MISO doesn't have an update to provide.
667232 KEEYASK6 138.80 | 1.0729 | 1.0661 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667247 KEEY_1-2_6 138.80 | 1.0709 | 1.0651 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667248 KEEY_3_6 138.80 | 1.0709 | 1.0651 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667249 KEEY_4_6 138.80 | 1.0708 | 1.065 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667250 KEEY_5_6 138.80 | 1.0729 | 1.0661 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667251 KEEY_6-7_6 138.80 | 1.0729 | 1.0661 | OPEN LINE FROM BUS 667035 [DORSEY 4 230.00] TO BUS 667037 [DC6 JCT4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
667301 POINTDB7 110.00 | 1.1252 | 1.125 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
667302 SLAVEFL7 110.00 | 1.1231 | 1.1228 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668047 LAVEREN7 110.00 | 1.0719 | 1.0708 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668049 PF-BK8 7 110.00 | 1.075 | 1.0745 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668050 PINEFLS7 110.00 | 1.075 | 1.0745 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668051 GULL LK7 110.00 | 1.0616 | 1.061 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668052 PA2-TAP7 110.00 | 1.075 | 1.0745 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668053 ABIT-1 7 110.00 | 1.075 | 1.0746 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668057 PA1-TAP7 110.00 | 1.075 | 1.0745 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668058 ABIT-2 7 110.00 | 1.075 | 1.0746 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668061 PF-BK7 7 110.00 | 1.075 | 1.0746 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668062 GREATFL7 110.00 | 1.0841 | 1.0839 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668064 RAVLAKE7 110.00 | 0.9123 | 1.0088 | OPEN LINE FROM BUS 667064 [RAVLAKE4 230.00] TO BUS 668064 [RAVLAKE7 110.00] TO BUS 669143 [RAVLKB39 13.800] CKT 3 | MH violation: MISO doesn't have an update to provide.
668075 LACDUBN7 110.00 | 1.0694 | 1.0693 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668077 SG12 TP7 110.00 | 1.0705 | 1.0705 | BASE CASE | MH violation: MISO doesn't have an update to provide.
668078 MCARTHR7 110.00 | 1.0834 | 1.0832 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668079 MCARTH27 110.00 | 1.0834 | 1.0832 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668080 MCARTH17 110.00 | 1.0833 | 1.0832 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668081 7SISTER7 110.00 | 1.082 | 1.082 | BASE CASE | MH violation: MISO doesn't have an update to provide.
668082 SR3SW3T7 110.00 | 1.082 | 1.082 | BASE CASE | MH violation: MISO doesn't have an update to provide.
668083 SK1 TP7 110.00 | 1.0822 | 1.0822 | BASE CASE | MH violation: MISO doesn't have an update to provide.
668084 SK1 SUB7 110.00 | 1.1543 | 1.1543 | BASE CASE | MH violation: MISO doesn't have an update to provide.
668085 BRERTON7 110.00 | 1.1473 | 1.1473 | BASE CASE | MH violation: MISO doesn't have an update to provide.
668086 STAR LK7 110.00 | 1.1424 | 1.1423 | OPEN LINE FROM BUS 608410 [WARRVRN2 500.00] TO BUS 608411 [WARRVRM2 500.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668089 VIVIAN 7 110.00 | 1.0643 | 1.0636 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668090 WHITESH7 110.00 | 1.0827 | 1.0826 | OPEN LINE FROM BUS 672621 [SHAND 4 230.00] TO BUS 672321 [SHAND 1G 18.000] CKT 1 | MH violation: MISO doesn't have an update to provide.
668091 WHSL1PH7 110.00 | 1.0894 | 1.0881 | OPEN LINE FROM BUS 667072 [WHTSL2 4 220.00] TO BUS 668092 [WHSL2PH7 110.00] CKT 8 | MH violation: MISO doesn't have an update to provide.
668092 WHSL2PH7 110.00 | 1.0894 | 1.0881 | OPEN LINE FROM BUS 667073 [WHTSL1 4 220.00] TO BUS 668091 [WHSL1PH7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668114 WILKES 7 110.00 | 1.0642 | 1.0629 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668115 WILK-TP7 110.00 | 1.0662 | 1.065 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668116 YV5-TP 7 110.00 | 1.0682 | 1.067 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668117 WILKES27 110.00 | 1.0665 | 1.0654 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668119 YM31TP 7 110.00 | 1.0755 | 1.0744 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668120 MORDEN 7 110.00 | 1.076 | 1.0749 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668121 ROSNFLD7 110.00 | 1.0748 | 1.0737 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668122 LOWEFRM7 110.00 | 1.0729 | 1.0718 | OPEN LINE FROM BUS 667043 [STVITAL4 230.00] TO BUS 668043 [STVITAL7 110.00] CKT 7 | MH violation: MISO doesn't have an update to provide.
668123 AUG B2 7 110.00 | 1.0633 | 1.0618 | OPEN LINE FROM BUS 667038 [ROSSER 4 230.00] TO BUS 668038 [ROSSER 7 110.00] TO BUS 669150 [ROSSER39 13.800] CKT 3 | MH violation: MISO doesn't have an update to provide.
668125 AUGIER 7 110.00 | 1.0651 | 1.0636 | OPEN LINE FROM BUS 667038 [ROSSER 4 230.00] TO BUS 668038 [ROSSER 7 110.00] TO BUS 669150 [ROSSER39 13.800] CKT 3 | MH violation: MISO doesn't have an update to provide.
668135 OVRFLWR7 110.00 | 1.0823 | 1.0576 | OPEN LINE FROM BUS 667059 [RALL 4 230.00] TO BUS 667060 [OVERFLO4 230.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668136 MANIGOT7 110.00 | 1.0692 | 1.0687 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
668149 SEDDONS7 110.00 | 1.0646 | 1.0646 | BASE CASE | MH violation: MISO doesn't have an update to provide.
668150 ANOLA 7 110.00 | 1.0614 | 1.0606 | OPEN LINE FROM BUS 657753 [RUNNING4 230.00] TO BUS 608751 [LITLFRK7 118.00] CKT 1 | MH violation: MISO doesn't have an update to provide.
672601 BD 4 230.00 | 1.088 | 1.088 | BASE CASE | SPC violation: MISO doesn't have an update to provide.
672602 BDX 4 230.00 | 1.0916 | 1.0731 | OPEN LINE FROM BUS 659372 [LARSON 4230.00] TO BUS 661084 [TIOGA4 4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672607 REGINA 4 230.00 | 1.0807 | 1.0755 | OPEN LINE FROM BUS 672642 [QE 3 4 230.00] TO BUS 672540 [QE 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672608 FLEETST4 230.00 | 1.0783 | 1.0719 | OPEN LINE FROM BUS 672642 [QE 3 4 230.00] TO BUS 672540 [QE 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672609 KENNEDY4 230.00 | 1.0632 | 1.0543 | OPEN LINE FROM BUS 672614 [TANTALL4 230.00] TO BUS 672620 [MOSIACK3 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672610 POPLAR 4 230.00 | 1.0913 | 1.0913 | BASE CASE | SPC violation: MISO doesn't have an update to provide.
672612 CONDIE 4 230.00 | 1.0837 | 1.0747 | OPEN LINE FROM BUS 672642 [QE 3 4 230.00] TO BUS 672540 [QE 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672613 AUBURNT4 230.00 | 1.0631 | 1.0293 | OPEN LINE FROM BUS 667067 [RESTON 4 230.00] TO BUS 672613 [AUBURNT4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672616 PEEBLES4 230.00 | 1.0881 | 1.0692 | OPEN LINE FROM BUS 672609 [KENNEDY4 230.00] TO BUS 672616 [PEEBLES4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672617 KEND-TAP 230.00 | 1.0879 | 1.0751 | OPEN LINE FROM BUS 672609 [KENNEDY4 230.00] TO BUS 672616 [PEEBLES4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672621 SHAND 4 230.00 | 1.0913 | 1.0913 | BASE CASE | SPC violation: MISO doesn't have an update to provide.
672630 EBCAMPB4 230.00 | 1.078 | 1.078 | BASE CASE | SPC violation: MISO doesn't have an update to provide.
672635 BETHUNETAP 230.00 | 1.0802 | 1.0704 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672636 BETHUNE 230.00 | 1.08 | 1.0702 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672638 BEATTY 4 230.00 | 1.0744 | 1.0719 | OPEN LINE FROM BUS 672650 [NIPAWIN4 230.00] TO BUS 672352 [NIPAWI3G 13.800] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672642 QE 3 4 230.00 | 1.1318 | 1.0509 | OPEN LINE FROM BUS 672642 [QE 3 4 230.00] TO BUS 672540 [QE 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672649 CODETTE4 230.00 | 1.0854 | 1.0848 | OPEN LINE FROM BUS 672630 [EBCAMPB4 230.00] TO BUS 672649 [CODETTE4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672650 NIPAWIN4 230.00 | 1.087 | 1.087 | BASE CASE | SPC violation: MISO doesn't have an update to provide.
672651 MAIDNORTH 230.00 | 1.0706 | 1.0666 | OPEN LINE FROM BUS 672651 [MAIDNORTH 230.00] TO BUS 672696 [BRADA 4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672656 NEWBPSS 230.00 | 1.079 | 1.07 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672664 ROWATT 230.00 | 1.0818 | 1.0768 | OPEN LINE FROM BUS 672642 [QE 3 4 230.00] TO BUS 672540 [QE 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672666 LLOYDMI4 230.00 | 1.075 | 1.075 | BASE CASE | SPC violation: MISO doesn't have an update to provide.
672670 COTEAU 4 230.00 | 1.0882 | 1.0622 | OPEN LINE FROM BUS 672670 [COTEAU 4 230.00] TO BUS 672570 [COTEAU 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672682 LIEB-TAP 230.00 | 1.081 | 1.0723 | OPEN LINE FROM BUS 672685 [SWIFTCU4 230.00] TO BUS 672585 [SWIFTCU6 138.00] CKT 2 | SPC violation: MISO doesn't have an update to provide.
672683 MCNEILL4 230.00 | 1.0818 | 1.0731 | OPEN LINE FROM BUS 672685 [SWIFTCU4 230.00] TO BUS 672585 [SWIFTCU6 138.00] CKT 2 | SPC violation: MISO doesn't have an update to provide.
672684 RUSHLAK4 230.00 | 1.1011 | 1.0784 | OPEN LINE FROM BUS 672684 [RUSHLAK4 230.00] TO BUS 672685 [SWIFTCU4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672685 SWIFTCU4 230.00 | 1.074 | 1.0657 | OPEN LINE FROM BUS 672685 [SWIFTCU4 230.00] TO BUS 672585 [SWIFTCU6 138.00] CKT 2 | SPC violation: MISO doesn't have an update to provide.
672686 ASSINIB4 230.00 | 1.0986 | 1.0897 | OPEN LINE FROM BUS 672684 [RUSHLAK4 230.00] TO BUS 672685 [SWIFTCU4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672688 PASQUA 4 230.00 | 1.0826 | 1.0713 | OPEN LINE FROM BUS 672688 [PASQUA 4 230.00] TO BUS 672588 [PASQUA 6 138.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
672697 ML EAST4 230.00 | 1.0721 | 1.0111 | OPEN LINE FROM BUS 672697 [ML EAST4 230.00] TO BUS 672698 [ML NRTH4 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
673601 KSY SUB TAP 230.00 | 1.0943 | 1.0801 | OPEN LINE FROM BUS 672616 [PEEBLES4 230.00] TO BUS 673601 [KSY SUB TAP 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.
673602 KISBEY SUB S230.00 | 1.0935 | 1.0793 | OPEN LINE FROM BUS 672616 [PEEBLES4 230.00] TO BUS 673601 [KSY SUB TAP 230.00] CKT 1 | SPC violation: MISO doesn't have an update to provide.

## PJM_N-1_VOLTAGE_WINTER
BUS | VCONT | VINIT | CONTINGENCY
94130 O66_NONFIRM 230.00 | 1.0538 | 1.0487 | L_H-2260
128819 HDSN_NONFIRM345.00 | 1.062 | 1.0569 | L_V-2301
200001 ALBURTIS 500.00 | 1.0858 | 1.0729 | PL100163
200002 BRANCHBG 500.00 | 1.0713 | 1.0671 | PJM23A
200003 BRIGHTON 500.00 | 1.0523 | 1.0464 | LN 543
200004 CNASTONE 500.00 | 1.0516 | 1.0475 | PJM77
200005 CONEM-GH 500.00 | 1.0672 | 1.0589 | PJM20A_CONEMAGH-KEYSTONE
200006 DEANS 500.00 | 1.0646 | 1.0621 | PJM23A
200007 ELROY 500.00 | 1.0755 | 1.0645 | PJM23A
200008 HOSENSAK 500.00 | 1.0772 | 1.0704 | PJM23A
200009 JUNIATA 500.00 | 1.0803 | 1.0752 | B2-TIE-230-103
200010 KEENEY 500.00 | 1.0541 | 1.0509 | PJM64
200011 KEYSTONE 500.00 | 1.0577 | 1.0522 | APS_B_G693
200012 NEWFRDM 500.00 | 1.0595 | 1.0534 | PJM81
200013 PEACHBTM 500.00 | 1.0588 | 1.0568 | PJM77
200014 SALEM 500.00 | 1.0573 | 1.0509 | PJM81
200015 WHITPAIN 500.00 | 1.063 | 1.0602 | PJM40A
200016 3 MILE I 500.00 | 1.077 | 1.0668 | PJM39-2
200017 SMITHBRG 500.00 | 1.0738 | 1.0638 | PJM_SMITHBRG_DEANS
200020 CLVT CLF 500.00 | 1.051 | 1.051 | BASE CASE
200021 SUNBURY 500.00 | 1.0937 | 1.0822 | 212340[PANDA]-1-GEN
200022 SUSQHANA 500.00 | 1.104 | 1.0903 | PL101385
200023 WESCOVLE 500.00 | 1.0856 | 1.0735 | PL100163
200024 LIMERICK 500.00 | 1.0623 | 1.0585 | PJM40A
200025 W CHAPEL 500.00 | 1.0573 | 1.0535 | PJM14
200026 HUNTERTN 500.00 | 1.05 | 1.05 | LN 226
200027 REDLION 500.00 | 1.0537 | 1.0497 | PJM81
200028 WINDSOR 500.00 | 1.0661 | 1.0614 | PJM89_A
200029 HOPECREEK 500.00 | 1.0573 | 1.051 | PJM81
200043 STEELCTY 500.00 | 1.0732 | 1.0631 | PJMA
200051 ROCKSPGS 500.00 | 1.0593 | 1.0583 | PJMC
200063 ORCHARD 500.00 | 1.0594 | 1.0532 | PJM81
200070 CENTERPT 500.00 | 1.0728 | 1.0621 | PJM23B
200074 LACKAW 500.00 | 1.1049 | 1.0864 | PL101385
200075 BREI 500.00 | 1.0856 | 1.0731 | PL100163
200076 NAMELESS 500.00 | 1.0635 | 1.0578 | PJM40A
200080 CORONA 500.00 | 1.0935 | 1.082 | 212340[PANDA]-1-GEN
200091 HOPATCONG 500.00 | 1.0821 | 1.075 | PL101385
200094 ROSELAND 500.00 | 1.0749 | 1.0694 | PL101385
200098 LACKJEFF_TIE500.00 | 1.1077 | 1.0791 | PJM JEFF-LACK 500_A
200099 N LANC 500.00 | 1.0781 | 1.0706 | PJM39-2
200100 CNASTCAP 500.00 | 1.0516 | 1.0475 | PJM77
200121 LIMCAP 500.00 | 1.0623 | 1.0585 | PJM40A
200122 P04 500.00 | 1.0584 | 1.0558 | P04-U
200181 ALB CAP 500.00 | 1.0873 | 1.0743 | PL100163
200182 CONEMCAP 500.00 | 1.0672 | 1.0589 | PJM20A_CONEMAGH-KEYSTONE
200183 JUN1 CAP 500.00 | 1.0803 | 1.0752 | B2-TIE-230-103
200184 TMI-CAP 500.00 | 1.077 | 1.0668 | PJM39-2
200185 HUNT-CAP 500.00 | 1.0521 | 1.0521 | P1-#..B3 MITCHELL 138/69 TB4
200187 SUSQ CAP 500.00 | 1.104 | 1.0903 | PL101385
200188 HUNT SVC 500.00 | 1.0502 | 1.05 | PJM17
200502 26BLAIN 115.00 | 0.9114 | 1.0079 | B3-PN-230-020A
200508 26HILL VAL 115.00 | 0.9171 | 0.9827 | B3-PN-230-020A
200512 26LEWISTWN 115.00 | 0.9167 | 1.0291 | B3-PN-230-020A
200518 26REED GAP 115.00 | 0.9159 | 1.0118 | B3-PN-230-020A
200519 26REED TAP 115.00 | 0.9165 | 1.0123 | B3-PN-230-020A
200521 26SAXTON 115.00 | 0.9018 | 0.9907 | B2-PN-115-079
200526 26THRE SPR 115.00 | 0.8943 | 0.9842 | B2-PN-115-079
200532 26ROXBURY 138.00 | 0.9199 | 0.9413 | B3-PN-230-020A
200799 26CEN.CTY 115.00 | 0.9214 | 1.0164 | B3-PN-115-028
200836 26STATHILL 115.00 | 0.9215 | 1.0222 | B3-PN-115-028
204530 27GERMANTN 138.00 | 0.92 | 0.9616 | B2-PE-138-028
204538 27STRABAN 115.00 | 1.0593 | 1.0002 | B3-ME-115-008
204619 27PORTLND 115.00 | 1.0555 | 1.0436 | B2-ME-115-030
204685 27ALBURTIS 230.00 | 1.0553 | 1.046 | B2-ME-230-002
207918 BLGR TR1 230.00 | 1.0552 | 1.0379 | PL101385
207919 BLGR TR2 230.00 | 1.0553 | 1.0379 | PL101385
207937 CLIN TR1 230.00 | 1.1009 | 1.0705 | 212340[PANDA]-1-GEN
207942 COLU TR1 230.00 | 1.1084 | 1.0842 | 212340[PANDA]-1-GEN
207943 COLU TR2 230.00 | 1.1082 | 1.0839 | 212340[PANDA]-1-GEN
207948 CUMB 230.00 | 1.0542 | 1.0438 | B2-TIE-230-103
207949 CUMB TR1 230.00 | 1.0539 | 1.0436 | B2-TIE-230-103
207950 CUMB TR2 230.00 | 1.0544 | 1.0439 | B2-TIE-230-103
207959 EPAL TR1 230.00 | 1.0688 | 1.0569 | PL101385
207960 EPAL TR2 230.00 | 1.0899 | 1.057 | PL100145
207964 ELDR TR1 230.00 | 1.1042 | 1.0853 | 212340[PANDA]-1-GEN
207965 ELDR TR2 230.00 | 1.1044 | 1.0854 | 212340[PANDA]-1-GEN
207968 ELIM 230.00 | 1.1027 | 1.0733 | 212340[PANDA]-1-GEN
207973 FRAC 230.00 | 1.113 | 1.0911 | PL100142
207974 FRAC TR2 230.00 | 1.1127 | 1.0909 | PL100142
207975 FRAC TR3 230.00 | 1.1127 | 1.0909 | PL100142
207977 HARW 230.00 | 1.0928 | 1.0771 | PL101385
207978 HARW TR5 230.00 | 1.0924 | 1.0768 | PL101385
207979 HARW EPA 230.00 | 1.0925 | 1.0769 | PL101385
207980 HARW SIE 230.00 | 1.0925 | 1.0768 | PL101385
207981 HARW SQ1 230.00 | 1.0924 | 1.0767 | PL101385
207982 HARW CAP 230.00 | 1.0934 | 1.0777 | PL101385
207999 JENK 230.00 | 1.0952 | 1.0635 | PL100353
208001 JENK TR2 230.00 | 1.095 | 1.0638 | PL100353
208004 JUNI BU1 230.00 | 1.0766 | 1.0607 | B2-TIE-230-103
208005 JUNI BU2 230.00 | 1.077 | 1.0609 | B2-TIE-230-103
208006 JUNI CAP 230.00 | 1.078 | 1.0618 | B2-TIE-230-103
208009 LACK 230.00 | 1.059 | 1.0303 | PL101385
208015 LYCO TR1 230.00 | 1.1031 | 1.0735 | 212340[PANDA]-1-GEN
208016 LYCO TR2 230.00 | 1.1033 | 1.0736 | 212340[PANDA]-1-GEN
208017 LYCO TR3 230.00 | 1.1033 | 1.0736 | 212340[PANDA]-1-GEN
208030 MLWD TR1 230.00 | 1.0774 | 1.0326 | PL100778
208034 MILT 230.00 | 1.0985 | 1.0759 | 212340[PANDA]-1-GEN
208040 MONT 230.00 | 1.1013 | 1.076 | 212340[PANDA]-1-GEN
208041 MONTSCR1 230.00 | 1.1013 | 1.076 | 212340[PANDA]-1-GEN
208042 MONTSCR2 230.00 | 1.1013 | 1.076 | 212340[PANDA]-1-GEN
208045 LAUS 230.00 | 1.056 | 1.0466 | PL100777
208046 POCO 230.00 | 1.0914 | 1.0545 | PL101216
208049 PAUP 230.00 | 1.0619 | 1.0395 | PL101385
208072 SIEG FRA 230.00 | 1.0608 | 1.0503 | PL101385
208073 SIEG TR1 230.00 | 1.0602 | 1.0498 | PL101385
208074 SIEG TR4 230.00 | 1.0608 | 1.0503 | PL101385
208075 SIEG TR5 230.00 | 1.0605 | 1.0501 | PL101385
208076 SIEG TR2 230.00 | 1.0605 | 1.0501 | PL101385
208077 SIEG TR3 230.00 | 1.0608 | 1.0503 | PL101385
208078 SAKR 230.00 | 1.0793 | 1.0635 | PL100777
208079 SAKR TR3 230.00 | 1.0791 | 1.063 | PL100778
208080 SAKR TR4 230.00 | 1.0788 | 1.0631 | PL100777
208082 SAKRCAPA 230.00 | 1.0802 | 1.0643 | PL100777
208083 SAKRCAPB 230.00 | 1.0802 | 1.0643 | PL100777
208087 SMAN TR3 230.00 | 1.0596 | 1.0499 | PL100777
208088 SMAN TR4 230.00 | 1.0653 | 1.0504 | PL100775
208089 SUGA 230.00 | 1.0929 | 1.0768 | PL101385
208090 SUMT 230.00 | 1.0632 | 1.0364 | PL101385
208092 ACAH 230.00 | 1.0882 | 1.065 | PL101216
208093 SUNO 230.00 | 1.09 | 1.07 | PL100353
208094 STAN 230.00 | 1.0962 | 1.0578 | PL100353
208095 STAN TR1 230.00 | 1.0961 | 1.058 | PL100353
208096 STAN TR2 230.00 | 1.0962 | 1.0581 | PL100353
208097 STAN TR3 230.00 | 1.0962 | 1.0581 | PL100353
208098 STAN TR4 230.00 | 1.0795 | 1.0569 | PL101385
208109 SUNB 230.00 | 1.0974 | 1.078 | 212340[PANDA]-1-GEN
208110 SUNBTR22 230.00 | 1.0974 | 1.078 | 212340[PANDA]-1-GEN
208111 SUNBTR23 230.00 | 1.0976 | 1.0782 | 212340[PANDA]-1-GEN
208113 SUSQ 230.00 | 1.0934 | 1.0761 | PL101385
208114 SUSQ G1 230.00 | 1.0935 | 1.0762 | PL101385
208116 SUSQTR21 230.00 | 1.0911 | 1.074 | PL101385
208117 SUSQ CAP 230.00 | 1.0948 | 1.0775 | PL101385
208120 SU10 230.00 | 1.0907 | 1.0733 | PL101385
208121 SU10TR10 230.00 | 1.0907 | 1.0733 | PL101385
208136 WSHO 230.00 | 1.0561 | 1.0437 | PL100605
208138 WSHO TR2 230.00 | 1.056 | 1.0437 | PL100605
208139 WSHO CAP 230.00 | 1.0571 | 1.0447 | PL100605
208301 DILL 1 138.00 | 0.8786 | 0.9784 | 208375(EPET 1)-208676(PACI 1)_1
208305 DNLY 1 138.00 | 0.5833 | 0.9848 | 208497(LAPR TP1)-208743(RTWN 1)_1
208306 DNLY 2 138.00 | 0.9189 | 0.987 | 208498(LAPR TP2)-208744(RTWN 2)_2
208308 DNLY 138.00 | 0.5832 | 0.9847 | 208497(LAPR TP1)-208743(RTWN 1)_1
208312 DOGR 1 138.00 | 0.9157 | 0.9777 | 208312(DOGR 1)-208641(NBRI 2)_2
208314 DOGR DC 138.00 | 0.9156 | 0.9776 | 208312(DOGR 1)-208641(NBRI 2)_2
208354 ELAN 1 138.00 | 0.9162 | 0.9774 | 208312(DOGR 1)-208641(NBRI 2)_2
208676 PACI 1 138.00 | 0.8783 | 0.9786 | 208375(EPET 1)-208676(PACI 1)_1
208692 PRIN SA1 138.00 | 0.9164 | 0.9773 | 208312(DOGR 1)-208641(NBRI 2)_2
208694 PRIN WH1 138.00 | 0.5894 | 0.9838 | 208497(LAPR TP1)-208743(RTWN 1)_1
208695 PRIN WH2 138.00 | 0.9197 | 0.9859 | 208498(LAPR TP2)-208744(RTWN 2)_2
208698 PRINUGS1 138.00 | 0.9163 | 0.9774 | 208312(DOGR 1)-208641(NBRI 2)_2
208700 PRINUGW1 138.00 | 0.5847 | 0.9846 | 208497(LAPR TP1)-208743(RTWN 1)_1
208701 PRINUGW2 138.00 | 0.9191 | 0.9867 | 208498(LAPR TP2)-208744(RTWN 2)_2
208743 RTWN 1 138.00 | 0.5827 | 0.9856 | 208497(LAPR TP1)-208743(RTWN 1)_1
208744 RTWN 2 138.00 | 0.9187 | 0.9873 | 208498(LAPR TP2)-208744(RTWN 2)_2
210623 ELHE 1 69.000 | 0.9093 | 0.9466 | B2-ME-230-023
210624 ELHE 2 69.000 | 0.9018 | 0.9398 | B2-ME-230-023
210634 ELRO T12 138.00 | 0.9448 | 0.9806 | PJM22
210638 ELRO T34 138.00 | 0.9448 | 0.9806 | PL100165
210791 BING TP2 69.000 | 0.9103 | 0.9479 | B2-ME-230-023
210792 BING TP1 69.000 | 0.913 | 0.9501 | B2-ME-230-023
210794 LANA 2 69.000 | 0.9189 | 0.956 | B2-ME-230-023
211169 SALL 69.000 | 0.9115 | 0.9487 | B2-ME-230-023
211593 HARW4 230.00 | 1.0909 | 1.0768 | PL101385
211594 HARW5 230.00 | 1.0907 | 1.0765 | PL101385
211595 HARW6 230.00 | 1.0907 | 1.0767 | PL101385
212340 PANDA 230.00 | 1.1012 | 1.0716 | 212340[PANDA]-1-GEN
212397 SAEG 230.00 | 1.1012 | 1.0707 | 212340[PANDA]-1-GEN
216900 ATHENIA 230.00 | 1.054 | 1.0497 | L_B-1302
216908 BAYONNE 345.00 | 1.0628 | 1.0542 | T_LIND3_2301
216917 ERUTHF_2 138.00 | 1.0515 | 1.0268 | T_ATHN_220-1
216993 NORTHAV 345.00 | 1.0614 | 1.0512 | T_LIND3_2301
217009 BERGFIELD 230.00 | 1.0537 | 1.0493 | L_B-1302
217010 NMILFRD 230.00 | 1.0537 | 1.0494 | L_B-1302
217011 MAYWOOD_1 230.00 | 1.0542 | 1.0499 | L_B-1302
217012 SADDLBRK_6 230.00 | 1.0544 | 1.05 | L_B-1302
217013 HILLSDALE 230.00 | 1.0529 | 1.049 | L_B-1302
217015 FAIRLAWN_5 138.00 | 1.0598 | 1.0371 | T_ATHN_220-1
217020 NEWARK_1 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
217022 NEWARK_3 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
217023 BAYONNE_COG 138.00 | 1.0641 | 1.0561 | T_LIND3_2301
217045 ESSEX_4 138.00 | 1.0752 | 1.0335 | T_ESX_220-1
217047 FAIRLAWN_2 138.00 | 1.0598 | 1.0371 | T_ATHN_220-1
217048 FAIRLAWN_4 138.00 | 1.0598 | 1.0371 | T_ATHN_220-1
217049 FOUNDRY_1 138.00 | 1.0619 | 1.039 | T_ESX_220-1
217056 DORMPL_1 138.00 | 1.0593 | 1.0411 | T_ESX_220-1
217057 NEWARK_4 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
217058 MARION 345.00 | 1.0622 | 1.0541 | T_LIND3_2301
217065 ECRR_1 138.00 | 1.0629 | 1.0388 | T_ESX_220-1
217070 CLIFTON_B 230.00 | 1.0532 | 1.0491 | L_B-1302
217071 CLIFTON_K 230.00 | 1.0532 | 1.049 | L_B-1302
217088 KULLERRD_3 138.00 | 1.0559 | 1.0292 | T_ATHN_220-1
217089 LEONIA_2 230.00 | 1.0537 | 1.0487 | L_H-2260
217100 BERGEN 230.00 | 1.0535 | 1.0484 | L_H-2260
217107 FAIRLAWN_1 138.00 | 1.0598 | 1.0371 | T_ATHN_220-1
217119 FEDERLSQ 138.00 | 1.0606 | 1.0398 | T_ESX_220-1
217134 BAYWAY 345.00 | 1.0608 | 1.0503 | T_LIND3_2301
217158 BERGEN_M 138.00 | 1.0578 | 1.0395 | T_ATHN_220-1
217159 ESSEX_C 138.00 | 1.063 | 1.0388 | T_ESX_220-1
217178 Q206_HUDSNDC345.00 | 1.062 | 1.0569 | L_V-2301
217304 ERUTHF_1 138.00 | 1.0515 | 1.0268 | T_ATHN_220-1
217306 KULLERRD_1 138.00 | 1.0559 | 1.0292 | T_ATHN_220-1
217307 MAYWOOD_2 230.00 | 1.0542 | 1.0499 | L_B-1302
217323 ECRR_2 138.00 | 1.0629 | 1.0388 | T_ESX_220-1
217326 ESSEX_3 138.00 | 1.0752 | 1.0335 | T_ESX_220-1
217329 FEDERLSQ_2 138.00 | 1.0606 | 1.0398 | T_ESX_220-1
217869 AIRPORT 345.00 | 1.0614 | 1.0511 | T_LIND3_2301
217920 SADDLBRK_1 230.00 | 1.0544 | 1.05 | L_B-1302
217922 SADDLBRK_3 230.00 | 1.0544 | 1.05 | L_B-1302
217923 SADDLBRK_4 230.00 | 1.0544 | 1.05 | L_B-1302
217924 SADDLBRK_5 230.00 | 1.0544 | 1.05 | L_B-1302
217936 LEONIA_1 230.00 | 1.0537 | 1.0487 | L_H-2260
217955 BAYWAY_K 138.00 | 1.0605 | 1.0453 | T_ESX_220-1
217959 BAYONNE_A 138.00 | 1.0638 | 1.0557 | T_LIND3_2301
218224 BERGEN_REAC 230.00 | 1.0535 | 1.0484 | L_H-2260
219119 TRENTON_H 230.00 | 1.0569 | 1.0378 | L_A-2201
219746 MERCER_1 230.00 | 1.057 | 1.0344 | L_A-2201
219749 MERCER_5 230.00 | 1.057 | 1.0344 | L_A-2201
220410 N.WEST230-3 230.00 | 1.1188 | 1.0271 | BG_CKT2371
220947 NWEST3CP 230.00 | 1.1215 | 1.0295 | BG_CKT2371
221021 DORSY T2 115.00 | 1.0525 | 1.0433 | HIRDG_230-4
221065 FINKS573 115.00 | 1.0606 | 1.0038 | BG_CKT2371
221078 MT.WASH702 115.00 | 1.0408 | 1.0297 | BG_110701
221120 HANOVR.T 115.00 | 1.0598 | 1.0034 | BG_CKT2371
221196 DORSY.R1 115.00 | 1.0528 | 1.0468 | BG_CKT2314
221199 H.RDGE-5 115.00 | 1.0544 | 1.049 | PP27
221200 H.RDGE-4 115.00 | 1.0528 | 1.0441 | HIRDG_230-4
221201 CRYSPR41 115.00 | 1.0528 | 1.0469 | PP27
221202 CRYSPR42 115.00 | 1.0524 | 1.0432 | HIRDG_230-4
221203 W.ROCK70 115.00 | 1.0594 | 0.9998 | BG_CKT2371
221207 WESTMN71 115.00 | 1.0595 | 0.9972 | BG_CKT2371
221208 DEER.P71 115.00 | 1.0608 | 1.003 | BG_CKT2371
221209 W.ROCK71 115.00 | 1.0602 | 1.0024 | BG_CKT2371
221247 CAMPSML 115.00 | 1.0418 | 1.0301 | BG_110701
230900 WY138CAP 138.00 | 1.0753 | 1.0739 | PJM79
230914 HARM_CAP 138.00 | 1.0582 | 1.0514 | CKT 23012
230915 CHAP_CAP 138.00 | 1.0579 | 1.052 | CKT 23012
230916 KEEN_CAP 138.00 | 1.0563 | 1.05 | CKT 22074XX
230918 CHUR_CAP 138.00 | 1.0633 | 1.0616 | G_HOPC_G1
230919 STL_CAP 138.00 | 1.0629 | 1.0614 | CKT 13702
230920 MTPL_CAP 138.00 | 1.0625 | 1.0542 | CECIL AT20
230921 TWNS_CAP 138.00 | 1.0645 | 1.0603 | CKT 22074XX
230923 FELT_CAP 138.00 | 1.0616 | 1.0447 | CKT 13709
230925 NSEA_CAP 138.00 | 1.051 | 1.041 | CKT 13766
231100 TALLYVL 138.00 | 1.0646 | 1.0487 | EDGE MR AT20
231101 HOCKESSN 138.00 | 1.0544 | 1.0498 | CKT 23012
231102 VALLEYRD 138.00 | 1.058 | 1.0497 | EDGE MR AT20
231103 CARRCRFT 138.00 | 1.054 | 1.0494 | CKT 22084
231104 SILVRBRK 138.00 | 1.0558 | 1.0509 | CKT 13829
231105 W WILM 138.00 | 1.064 | 1.0513 | EDGE MR AT20
231106 WANAMKR 138.00 | 1.0641 | 1.0472 | EDGE MR AT20
231107 BRNDYWN4 138.00 | 1.064 | 1.0469 | EDGE MR AT20
231109 EDGEMR 4 138.00 | 1.0645 | 1.0465 | EDGE MR AT20
231110 MERMAID 138.00 | 1.0579 | 1.0495 | EDGE MR AT20
231111 MILLTOWN 138.00 | 1.0578 | 1.0494 | EDGE MR AT20
231112 CHRISTA 138.00 | 1.0614 | 1.0464 | EDGE MR AT20
231113 KIAMENSI 138.00 | 1.0578 | 1.0494 | EDGE MR AT20
231114 HARM_138 138.00 | 1.0574 | 1.0506 | CKT 23012
231115 CHAPLST 138.00 | 1.0573 | 1.0514 | CKT 23012
231116 CHRCHMNS 138.00 | 1.053 | 1.0462 | EDGE MR AT20
231117 BASIN RD 138.00 | 1.0544 | 1.0462 | EDGE MR AT20
231118 NEWCASTL 138.00 | 1.0562 | 1.0463 | EDGE MR AT20
231120 BEAR 138.00 | 1.0534 | 1.0466 | EDGE MR AT20
231121 HARES CR 138.00 | 1.0545 | 1.0472 | EDGE MR AT20
231122 KEENEYL 138.00 | 1.055 | 1.0484 | CECIL AT20
231123 KEEN_138 138.00 | 1.0564 | 1.0493 | CECIL AT20
231124 GLASGOW 138.00 | 1.0605 | 1.049 | CECIL AT20
231125 SUNSETLK 138.00 | 1.0551 | 1.0483 | CECIL AT20
231126 RL_138 138.00 | 1.0667 | 1.0535 | CKT 13818
231127 RL_138N 138.00 | 1.0549 | 1.0497 | CKT 23020
231128 REYBOLD 138.00 | 1.0559 | 1.0507 | CKT 23020
231129 LUMS 138.00 | 1.0601 | 1.052 | CKT 13841
231130 CECIL138 138.00 | 1.0645 | 1.0431 | CECIL AT20
231131 BLOOM ENRGY 138.00 | 1.0549 | 1.0497 | CKT 23020
231802 NCSTLCTY 138.00 | 1.0562 | 1.0463 | EDGE MR AT20
231803 MOTIVA 138.00 | 1.0554 | 1.0502 | CKT 23020
231814 NCCTYTAP 138.00 | 1.0552 | 1.0466 | EDGE MR AT20
232100 CHURCH 138.00 | 1.0647 | 1.0612 | CHURCH AT2
232101 WYEMILLS 138.00 | 1.075 | 1.0735 | 231914 HR8 18
232102 HILLSBRO 138.00 | 1.0674 | 1.066 | CKT 13702
232103 STEEL138 138.00 | 1.0659 | 1.0605 | CKT 23076
232104 MT PLSNT 138.00 | 1.062 | 1.0538 | CECIL AT20
232106 MIDLTNTP 138.00 | 1.0625 | 1.056 | CECIL AT20
232107 TOWNSEND 138.00 | 1.0649 | 1.0598 | CECIL AT20
232112 FELTON 138.00 | 1.0608 | 1.044 | CKT 13709
232115 EASTON 138.00 | 1.0653 | 1.0614 | CKT 67BB
232118 NSEAFORD 138.00 | 1.0506 | 1.0406 | CKT 13766
232136 CONAWAY 138.00 | 1.0513 | 1.0317 | CKT 13766
232801 OIL_CITY 138.00 | 1.0658 | 1.0606 | CKT 23076
232804 MIDDLETN 138.00 | 1.0615 | 1.0549 | CECIL AT20
234250 MOUN-TAP 230.00 | 1.0982 | 1.0714 | PL100353
234251 MOUNT-H1 230.00 | 1.066 | 1.0469 | PL101385
234252 MOUNTAIN 230.00 | 1.0656 | 1.0463 | PL101385
234253 MOUNT-H2 230.00 | 1.0654 | 1.046 | PL101385
235101 01BEDNGT 500.00 | 1.0776 | 1.0602 | B2-PE-500-002
235103 01BLACKO 500.00 | 1.0787 | 1.049 | B2-WP-500-013
235105 01DOUBS 500.00 | 1.0665 | 1.0529 | LN 543
235106 01FMARTN 500.00 | 1.05 | 1.05 | TR12_CRTEC_B-S
235107 01HARRSN 500.00 | 1.05 | 1.05 | 4881_B1
235108 01HATFLD 500.00 | 1.0543 | 1.05 | B2-WP-500-007
235110 01MDWBRK 500.00 | 1.0559 | 1.0527 | LN 580
235111 01 502 J 500.00 | 1.0508 | 1.0497 | B3-TIE-765-502
235117 01KAMMER 500.00 | 1.055 | 1.0413 | B3-TIE-765-502
235118 01SOBEND 500.00 | 1.052 | 1.052 | G-6S 1POSSM6
235130 01BO SVC CAP500.00 | 1.0787 | 1.049 | B2-WP-500-013
235176 01EMERLD 138.00 | 0.8816 | 0.9886 | B2-WP-138-025
235182 01FRANKL 138.00 | 0.9203 | 0.9627 | B2-WP-138-001
235463 01TANEY 138.00 | 0.9159 | 0.9785 | B2-PE-138-028
235490 01MORGAN 138.00 | 0.8089 | 0.9727 | B2-PE-138-032
235519 01W WINC 138.00 | 0.9185 | 0.9801 | B2-PE-138-056
235546 01EAGLE 138.00 | 0.8989 | 0.9938 | B2-PE-138-022
235813 01PURSLEY 138.00 | 0.9202 | 0.9679 | B2-WP-138-001
235814 01CNX 138.00 | 0.9189 | 0.9614 | B2-WP-138-001
235837 01GRNGAP 500.00 | 1.0607 | 1.0503 | LN 572
235851 01NTHLNV 500.00 | 1.05 | 1.05 | HR2 GEN
237000 01BEDNGT CAP500.00 | 1.0846 | 1.0671 | B2-PE-500-002
237001 01B.O. CAP 500.00 | 1.0787 | 1.049 | B2-WP-500-013
237002 01DOUBS CAP 500.00 | 1.0796 | 1.0658 | LN 543
237004 01BO SVC IN 500.00 | 1.078 | 1.049 | B2-WP-500-013
237044 01MB CAP 500.00 | 1.063 | 1.063 | BASE CASE
242519 05CLOVRD 500.00 | 1.061 | 1.0589 | LN 566
242520 05J.FERR 500.00 | 1.0753 | 1.072 | 7421_B3_05CLOVRD 765-141
242976 05BUCYRC 138.00 | 0.9009 | 0.9844 | 716_B3_05HOWARD 138-1_WOMOAB
243091 05SCALDW 138.00 | 0.8895 | 0.9759 | 5717_B2_TOR728A_MOAB
243096 05SCUMBL 138.00 | 0.8784 | 0.9715 | 608_B3_05MUSKNG 138-1_WOMOAB
243117 05SULFRS 138.00 | 0.9001 | 0.989 | 716_B3_05HOWARD 138-1_WOMOAB
243118 05SUMMER 138.00 | 0.8808 | 0.9593 | 608_B3_05MUSKNG 138-1_WOMOAB
243123 05SWITZE 138.00 | 0.8977 | 0.9817 | 8893_B2_TOR778A_MOAB
245023 05TEBERN 138.00 | 0.8699 | 0.9493 | 608_B3_05MUSKNG 138-1_WOMOAB
247156 05STEAMT 138.00 | 0.8791 | 0.9601 | 608_B3_05MUSKNG 138-1_WOMOAB
247375 05BLUERACER8138.00 | 0.87 | 0.9494 | 608_B3_05MUSKNG 138-1_WOMOAB
247715 05BLUE RACER138.00 | 0.87 | 0.9494 | 608_B3_05MUSKNG 138-1_WOMOAB
254063 15CHSWK1 23.500 | 1.0542 | 1.0447 | P14_DRAVO_CAPS
270790 KATYDID ; B345.00 | 1.0534 | 1.0334 | 345-L19601_B-S
270904 TOP CROP ;P1345.00 | 1.0534 | 1.0334 | 345-L19601_B-S
270905 TOP CROP ;P2345.00 | 1.0535 | 1.0334 | 345-L19601_B-S
273153 FISK ; R12.500 | 1.0777 | 1.074 | 138-L0708__B-C
273163 A431-2 ; 13.200 | 1.0603 | 1.0588 | 138-L1603__R-N
273369 ESS J332 ;1 13.200 | 1.0513 | 1.0484 | JL-6U_______-S
274191 G385-2 ;1 34.000 | 1.0719 | 1.0698 | 138-L17715_R-C
274192 G385-2 ;2 34.000 | 1.0767 | 1.0734 | 076-L7615___
274244 ROCK FALL; 34.500 | 1.0546 | 1.0382 | 138-L15509GR-R
274674 JOLIET 9 ;6U18.000 | 0.8998 | 0.9039 | 138-L0901__B-S
274726 ZION EC ;2P18.000 | 1.0539 | 1.0425 | 974-U_ZIONE1-N
274727 ZION EC ;3P18.000 | 1.0544 | 1.0428 | 974-U_ZIONE1-N
274789 SE CHICAG;6U13.800 | 1.0581 | 1.0225 | CAP_SLINE_81-C
274790 SE CHICAG;7U13.800 | 1.0581 | 1.0225 | CAP_SLINE_81-C
274791 SE CHICAG;8U13.800 | 1.0581 | 1.0225 | CAP_SLINE_81-C
274792 SE CHICAG;9U13.800 | 1.058 | 1.0576 | 138-L0716__R-C
274793 SE CHICAG;0U13.800 | 1.058 | 1.0576 | 138-L0716__R-C
274794 SE CHICAG;1U13.800 | 1.058 | 1.0576 | 138-L0716__R-C
274795 SE CHICAG;2U13.800 | 1.058 | 1.0576 | 138-L0716__R-C
274826 FISK ;BP12.500 | 1.0614 | 1.039 | 274826[FISK ;BP]-P-GEN
274827 FISK ;RP12.500 | 1.0777 | 1.074 | 138-L0708__B-C
275153 RIDGELAND;2M69.000 | 1.0578 | 1.0551 | 138-L5105_GR-C
275159 RIDGELAND;4M69.000 | 1.0582 | 1.0555 | 138-L5105_GR-C
275319 STATELINE;1C34.500 | 1.0626 | 1.0348 | 138-L0708__B-C
292091 V1-030 CD 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
292092 V1-030 ED 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
292116 V1-030 CC 230.00 | 1.0535 | 1.0484 | L_H-2260
292191 V1-030 EC 230.00 | 1.0535 | 1.0484 | L_H-2260
292421 V3_017_TAP68230.00 | 1.054 | 1.0434 | V3_017_TAP86-V3-017
292423 V3_017_TAP86230.00 | 1.0557 | 1.0422 | V3_017_TAP86-MORGT230
292556 T157_TAP 500.00 | 1.0806 | 1.049 | LN 551
293428 V3-068 C 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
293429 V3-068 E 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
293433 V3-067 C 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
293434 V3-067 E 138.00 | 1.0607 | 1.0393 | T_ESX_220-1
293443 V3-065 C 138.00 | 1.0752 | 1.0335 | T_ESX_220-1
293444 V3-065 E 138.00 | 1.0752 | 1.0335 | T_ESX_220-1
313839 8PL VIEW_1 500.00 | 1.0514 | 1.0419 | LN 558
314898 8MT ST_1 500.00 | 1.05 | 1.05 | LN 222
314899 8MT ST_2 500.00 | 1.05 | 1.05 | LN 222
314903 8CHCKAHM 500.00 | 1.0525 | 1.0431 | LN 557
314906 8CLOVER 500.00 | 1.0592 | 1.0565 | LN 591
314912 8LEXNGTN 500.00 | 1.0533 | 1.0507 | LN 547
314917 8MT STM 500.00 | 1.05 | 1.05 | LN 222
314925 8PL VIEW 500.00 | 1.0514 | 1.0419 | LN 558
314936 8RAWLINGS 500.00 | 1.0535 | 1.045 | LN 591
314937 8MTSTORM2 500.00 | 1.05 | 1.05 | LN 222
314939 8GOOSE CREEK500.00 | 1.0514 | 1.0419 | LN 558
315856 8MTSTORMSVC1500.00 | 1.0501 | 1.05 | LN 529
341059 2BARREN CO 69.000 | 0.8692 | 0.9756 | 5BARREN CO-5SUMM SHADE
341080 2BECKTON 69.000 | 0.8743 | 0.9582 | 5BARREN CO-5SUMM SHADE
341149 2BON AYR 69.000 | 0.875 | 0.963 | 5BARREN CO-5SUMM SHADE
341272 2CAVE CITY 69.000 | 0.8673 | 0.9657 | 5BARREN CO-5SUMM SHADE
341275 2CAVE CITY J69.000 | 0.8686 | 0.9737 | 5BARREN CO-5SUMM SHADE
341491 2FOX HOLLOW 69.000 | 0.8866 | 0.9588 | 5BARREN CO-5SUMM SHADE
341530 2GLASGO-CLEV69.000 | 0.8806 | 0.957 | 5BARREN CO-5SUMM SHADE
341542 2GOODNIGHT 69.000 | 0.8711 | 0.9679 | 5BARREN CO-5SUMM SHADE
341548 2GORIN PRK J69.000 | 0.8828 | 0.961 | 5BARREN CO-5SUMM SHADE
341647 2HORSE CV KU69.000 | 0.8522 | 0.9539 | 5BARREN CO-5SUMM SHADE
341650 2HORSECAVE T69.000 | 0.8565 | 0.9578 | 5BARREN CO-5SUMM SHADE
341651 2HORSECAVE J69.000 | 0.8565 | 0.9578 | 5BARREN CO-5SUMM SHADE
341908 2MUNFVIL EK 69.000 | 0.902 | 0.9791 | 5BARREN CO-5SUMM SHADE
341911 2MUNFVIL KU 69.000 | 0.8888 | 0.9722 | 5BARREN CO-5SUMM SHADE
341914 2MUNFVILKU T69.000 | 0.8895 | 0.9729 | 5BARREN CO-5SUMM SHADE
342037 2PARKWAY 1 69.000 | 0.8788 | 0.9516 | 5BARREN CO-5SUMM SHADE
342040 2PARKWAY 2 69.000 | 0.8787 | 0.9515 | 5BARREN CO-5SUMM SHADE
342043 2PARKWAY 2 T69.000 | 0.8808 | 0.957 | 5BARREN CO-5SUMM SHADE
342049 2PATTON RD J69.000 | 0.915 | 0.9695 | 5BARREN CO-5SUMM SHADE
342238 2SEYMOUR 69.000 | 0.8666 | 0.9719 | 5BARREN CO-5SUMM SHADE
342241 2SEYMOUR T 69.000 | 0.8684 | 0.9735 | 5BARREN CO-5SUMM SHADE
342442 2W GLASGOW 69.000 | 0.8743 | 0.9528 | 5BARREN CO-5SUMM SHADE
342445 2W GLASGOW T69.000 | 0.8779 | 0.9562 | 5BARREN CO-5SUMM SHADE
907991 X1-078 500.00 | 1.0646 | 1.0621 | PJM23A
909022 X2-012 E 230.00 | 1.1012 | 1.0716 | 212340[PANDA]-1-GEN
912052 X4-006 E 230.00 | 1.0557 | 1.0444 | V3_017_TAP86-V3-017
912130 X4-020 TAP 500.00 | 1.0776 | 1.0632 | PJM39-2
913271 Y1-065 C 500.00 | 1.064 | 1.064 | DAY_11
913272 Y1-065 E 500.00 | 1.064 | 1.064 | S121-G10
914031 Y2-015 C 230.00 | 1.1084 | 1.0888 | 212340[PANDA]-1-GEN
914032 Y2-015 E 230.00 | 1.1084 | 1.0888 | 212340[PANDA]-1-GEN
914271 Y2-089 230.00 | 1.059 | 1.0303 | PL101385
915191 Y3-043 500.00 | 1.06 | 1.06 | TR81_WOLFS_B-N
915681 Y3-102 500.00 | 1.06 | 1.0595 | PJM78

## SPP_N-1_VOLTAGE_WINTER
BUS | VCONT pu | VINIT pu | CONTINGENCY
508349 NMINEOL4 138.00 | 0.9492 | 0.9766 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508357 BURGEST4 138.00 | 0.939 | 0.9737 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508358 LHAWKIN4 138.00 | 0.948 | 0.9741 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508360 EBURGES4 138.00 | 0.9381 | 0.9728 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508361 STARR 4 138.00 | 0.9377 | 0.9724 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508362 BENWHEL4 138.00 | 0.8964 | 0.9509 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508363 KENSULI4 138.00 | 0.9031 | 0.952 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508364 GARDVAL4 138.00 | 0.9088 | 0.9535 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508365 PECANHL4 138.00 | 0.9225 | 0.9604 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508366 REDSPRW4 138.00 | 0.9372 | 0.968 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
508367 SANDSPR4 138.00 | 0.9462 | 0.9754 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509240 CROCKET4 138.00 | 0.8449 | 1.001 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509242 JACKSNV4 138.00 | 0.8969 | 0.9683 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509244 ANTIOCH4 138.00 | 0.9009 | 0.9623 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509246 BARTONC4 138.00 | 0.897 | 0.9535 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509247 CANTON 4 138.00 | 0.919 | 0.9677 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509248 CANTONT4 138.00 | 0.9318 | 0.972 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509249 CEDAR 4 138.00 | 0.9007 | 0.9537 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509250 COFFEE 4 138.00 | 0.8946 | 0.9613 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509251 EXPLORE4 138.00 | 0.9217 | 0.9703 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509252 GLENPIN4 138.00 | 0.9258 | 0.9711 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509253 JACKSON4 138.00 | 0.9196 | 0.9682 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509254 MABANK 4 138.00 | 0.9136 | 0.9635 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509255 NEWYORK4 138.00 | 0.8969 | 0.9601 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509256 WALTON 4 138.00 | 0.8977 | 0.9527 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509257 DVARANT4 138.00 | 0.901 | 0.9624 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509258 DVARGP 4 138.00 | 0.9259 | 0.9712 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509320 ALTO 4 138.00 | 0.864 | 0.9804 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509321 BEREA 4 138.00 | 0.844 | 1.0003 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509322 GRAPLND4 138.00 | 0.8479 | 0.9947 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509323 LATEXO 4 138.00 | 0.8454 | 0.9993 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509324 PINEGRV4 138.00 | 0.8799 | 0.9729 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509325 MUSTPR4 138.00 | 0.8438 | 0.9981 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
509326 SLOCUM 4 138.00 | 0.8511 | 0.99 | OPEN LINE FROM BUS 509241 [CROCKET7 345.00] TO BUS 509240 [CROCKET4 138.00] TO BUS 509243 [CROCK-B1 13.800] CKT 1
515458 BORDER 7345.00 | 1.0524 | 1.0237 | OPEN LINE FROM BUS 515375 [WWRDEHV7 345.00] TO BUS 515458 [BORDER 7345.00] CKT 1
515554 BVRCNTY7 345.00 | 1.0502 | 1.0459 | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1
523095 HITCHLAND 6230.00 | 1.0545 | 1.0382 | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1
523240 RB-EXUM 3115.00 | 0.948 | 1.0053 | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6230.00] TO BUS 523308 [MOORE_E 3115.00] TO BUS 523302 [MOORE_TR1 113.200] CKT 1
523256 ETTER 3115.00 | 0.9465 | 1.0092 | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6230.00] TO BUS 523308 [MOORE_E 3115.00] TO BUS 523302 [MOORE_TR1 113.200] CKT 1
523277 VALERO 3115.00 | 0.9378 | 1.0051 | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6230.00] TO BUS 523308 [MOORE_E 3115.00] TO BUS 523302 [MOORE_TR1 113.200] CKT 1
523304 MOORE_W 3115.00 | 0.9403 | 1.0073 | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6230.00] TO BUS 523308 [MOORE_E 3115.00] TO BUS 523302 [MOORE_TR1 113.200] CKT 1
523308 MOORE_E 3115.00 | 0.9403 | 1.0073 | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6230.00] TO BUS 523308 [MOORE_E 3115.00] TO BUS 523302 [MOORE_TR1 113.200] CKT 1
523315 RB-S&S 3115.00 | 0.9395 | 1.0036 | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6230.00] TO BUS 523308 [MOORE_E 3115.00] TO BUS 523302 [MOORE_TR1 113.200] CKT 1
523318 DUMAS_19ST 3115.00 | 0.9401 | 0.9922 | OPEN LINE FROM BUS 523309 [MOORE_CNTY 6230.00] TO BUS 523308 [MOORE_E 3115.00] TO BUS 523302 [MOORE_TR1 113.200] CKT 1
523551 HUTCHISON 6230.00 | 0.9472 | 0.9782 | OPEN LINE FROM BUS 523551 [HUTCHISON 6230.00] TO BUS 524044 [NICHOLS 6230.00] CKT 1
523853 FINNEY 7345.00 | 1.0882 | 1.027 | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1
524163 EAST_PLANT 6230.00 | 0.9021 | 0.9852 | OPEN LINE FROM BUS 523977 [HARRNG_WST 6230.00] TO BUS 524163 [EAST_PLANT 6230.00] CKT 1
525549 TOLK 7345.00 | 1.0858 | 1.0194 | OPEN LINE FROM BUS 525543 [TOLK_TAP 6230.00] TO BUS 525549 [TOLK 7345.00] TO BUS 525537 [TOLK_TR 113.200] CKT 1
527276 SEMINOLE 6230.00 | 0.9236 | 0.9889 | OPEN LINE FROM BUS 527149 [MUSTANG 6230.00] TO BUS 527276 [SEMINOLE 6230.00] CKT 1
527340 DOSS 3115.00 | 0.9454 | 0.9955 | OPEN LINE FROM BUS 527149 [MUSTANG 6230.00] TO BUS 527276 [SEMINOLE 6230.00] CKT 1
527346 LEGACY 3115.00 | 0.9468 | 0.9931 | OPEN LINE FROM BUS 527149 [MUSTANG 6230.00] TO BUS 527276 [SEMINOLE 6230.00] CKT 1
527802 EDDY_CNTY 7345.00 | 1.0986 | 1.0049 | OPEN LINE FROM BUS 527799 [EDDY_NORTH 6230.00] TO BUS 527802 [EDDY_CNTY 7345.00] TO BUS 527796 [EDDY_TR 113.200] CKT 1
527953 LIVSTNRIDGE3115.00 | 0.7687 | 0.971 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527955 SAGE_BRUSH 3115.00 | 0.7724 | 0.9511 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527957 LAGARTO 3115.00 | 0.7857 | 0.9489 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
527999 INTREPDW_TP3115.00 | 0.9395 | 1.0048 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528000 INTREPIDWST3115.00 | 0.9387 | 1.004 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528009 WIPP 3115.00 | 0.7469 | 0.9752 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528016 SAND_DUNES 3115.00 | 0.7013 | 0.9785 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528018 RED_BLUFF 3115.00 | 0.655 | 0.9902 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528020 BOPCO_PKRLK3115.00 | 0.6923 | 0.9816 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528025 RDRUNNER 3115.00 | 0.6224 | 0.9954 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528027 RDRUNNER 7345.00 | 0.5658 | 0.9699 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528035 IMC_#1_TP 3115.00 | 0.882 | 0.9916 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528037 IMC_#1 3115.00 | 0.8811 | 0.9909 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528040 BATTLE_AXE 3115.00 | 0.6002 | 0.982 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528222 CHINA_DRAW 3115.00 | 0.8907 | 1.0095 | OPEN LINE FROM BUS 528185 [NLOV_PLT 7345.00] TO BUS 528223 [CHINA_DRAW 7345.00] CKT 1
528223 CHINA_DRAW 7345.00 | 0.8851 | 1.0207 | OPEN LINE FROM BUS 528185 [NLOV_PLT 7345.00] TO BUS 528223 [CHINA_DRAW 7345.00] CKT 1
528228 WOOD_DRAW 3115.00 | 0.7338 | 0.9797 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528230 AGAVE_RHILL3115.00 | 0.6162 | 0.9573 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528232 OCHOA 3115.00 | 0.6168 | 0.9565 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528239 PNDEROSATP 3115.00 | 0.6641 | 0.9462 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528240 PONDEROSA 3115.00 | 0.6563 | 0.9408 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528246 YESO_HILLS 3115.00 | 0.8718 | 0.9933 | OPEN LINE FROM BUS 528185 [NLOV_PLT 7345.00] TO BUS 528223 [CHINA_DRAW 7345.00] CKT 1
528406 MALJMAR1&2 3115.00 | 0.9436 | 0.9785 | OPEN LINE FROM BUS 527896 [HOBBS_INT 7345.00] TO BUS 527965 [KIOWA 7345.00] CKT 1
528505 LEA_ROAD 3115.00 | 0.8141 | 0.9605 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528512 EUNICE 3115.00 | 0.9333 | 0.987 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528519 WARD 3115.00 | 0.7656 | 0.9533 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528526 TEAGUE 3115.00 | 0.7965 | 0.9554 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528533 DRINKARD_TP3115.00 | 0.9351 | 0.9888 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528540 WHITTEN 3115.00 | 0.7107 | 0.9467 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528547 S_JAL 3115.00 | 0.7372 | 0.9442 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528552 OIL_CENTER 3115.00 | 0.8465 | 0.9689 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528554 COOPER_RNCH3115.00 | 0.8673 | 0.9744 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528561 DOLLARHIDE 3115.00 | 0.7255 | 0.9355 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528564 TOBOSOFLATS3115.00 | 0.7186 | 0.9303 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528568 MONUMNT_TP 3115.00 | 0.9437 | 0.9976 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528582 BYRD 3115.00 | 0.9085 | 0.9861 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528589 DRINKARD 3115.00 | 0.9305 | 0.9886 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528596 CARDINAL 3115.00 | 0.8398 | 0.9646 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528602 ANDREWS 3115.00 | 0.9231 | 0.9876 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528603 NA_ENRICH 3115.00 | 0.9132 | 0.9857 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
528604 ANDREWS 6230.00 | 0.9474 | 0.9994 | OPEN LINE FROM BUS 527894 [HOBBS_INT 6230.00] TO BUS 528604 [ANDREWS 6230.00] CKT 1
528605 TARGA 3115.00 | 0.8684 | 0.9721 | OPEN LINE FROM BUS 527965 [KIOWA 7345.00] TO BUS 528027 [RDRUNNER 7345.00] CKT 1
530554 ATWOOD 3 115.00 | 0.9404 | 0.9977 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530555 COLBY 3 115.00 | 0.9442 | 1.0174 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530556 HOXIE 3 115.00 | 0.9439 | 1.0002 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530559 PH RUN 3 115.00 | 0.9432 | 1.0047 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530621 PAWNEE 3 115.00 | 0.9451 | 0.9765 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
530682 SEGNTP 3 115.00 | 0.9441 | 1.0058 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530683 SEGUIN 3 115.00 | 0.9438 | 1.0054 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
530685 LARNED3 115.00 | 0.9447 | 0.976 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
531220 HERNTAP3 115.00 | 0.9419 | 0.9962 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531351 BREWSTR3 115.00 | 0.9427 | 1.0131 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531353 GOODLND3 115.00 | 0.9407 | 1.0093 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531354 KANARAD3 115.00 | 0.9484 | 1.0081 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531355 NSI 115.00 | 0.9447 | 1.0078 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531356 NSI TAP3 115.00 | 0.9449 | 1.008 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531357 RULETON3 115.00 | 0.9417 | 1.0079 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531364 ATWODSW3 115.00 | 0.9415 | 0.9966 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531365 BIRDCTY3 115.00 | 0.9398 | 1.0018 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531367 HERNDON3 115.00 | 0.9456 | 0.9971 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531368 LAWNRID3 115.00 | 0.9392 | 1.0045 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531369 NATWOOD3 115.00 | 0.9414 | 0.9965 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531370 STFRAN 3 115.00 | 0.9391 | 1.0026 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531411 GOVE 3 115.00 | 0.9474 | 1.0015 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531412 GRINNEL3 115.00 | 0.944 | 1.0028 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531429 MINGO 3 115.00 | 0.9488 | 1.0232 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531441 CSTFRAN3 115.00 | 0.939 | 1.0028 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531443 GODLNDT3 115.00 | 0.9406 | 1.009 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531444 GOODCTY3 115.00 | 0.9382 | 1.0068 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531471 STFRANT3 115.00 | 0.9391 | 1.0029 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531487 MCDONLD3 115.00 | 0.9399 | 0.9996 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531488 BVERVLLY 115.00 | 0.9401 | 0.9993 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
531489 ONEOK 3 115.00 | 0.9399 | 0.9992 | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531429 [MINGO 3 115.00] TO BUS 531452 [MINGTER1 13.800] CKT 1
532769 LANG 7 345.00 | 0.9283 | 1.0085 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
532996 TIOGA 4 138.00 | 0.9248 | 0.9569 | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] CKT 1
532996 TIOGA 4 138.00 | 0.9442 | 0.9569 | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510379 [DELWARE4 138.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1
532996 TIOGA 4 138.00 | 0.95 | 0.9569 | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1
533001 ALTOONA4 138.00 | 0.9489 | 0.9669 | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] CKT 1
533004 MONTGOM4 138.00 | 0.9482 | 0.9708 | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510379 [DELWARE4 138.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1
533006 TAYLOR 4 138.00 | 0.9486 | 0.9705 | OPEN LINE FROM BUS 510380 [DELWARE7 345.00] TO BUS 510379 [DELWARE4 138.00] TO BUS 510370 [DELAWAR1 13.800] CKT 1
533302 EEUREKA3 115.00 | 0.9452 | 1.0015 | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1
539631 FLATRWD3 138.00 | 0.9479 | 1.0084 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539638 FLATRDG3 138.00 | 0.9478 | 1.0084 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539649 SAWYER 3 115.00 | 0.9472 | 0.9911 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539651 RVROAD 115.00 | 0.9478 | 0.9887 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539673 MED-LDG3 115.00 | 0.9447 | 0.9986 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539674 BARBER 4 138.00 | 0.9461 | 1.0024 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539687 PRATT 3 115.00 | 0.9478 | 0.9887 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539760 BARBER 3 115.00 | 0.9446 | 0.9987 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
539804 THISTLE4 138.00 | 0.9478 | 1.0098 | OPEN LINE FROM BUS 539801 [THISTLE7 345.00] TO BUS 539804 [THISTLE4 138.00] TO BUS 539802 [THISTLE T1 13.800] CKT 1
541197 MULLNCR7 345.00 | 1.0535 | 1.0392 | OPEN LINE FROM BUS 541197 [MULLNCR7 345.00] TO BUS 541357 [MULLNCR2 69.000] TO BUS 541373 [MULLNCR1 13.800] CKT 1
547479 LAR382 5 161.00 | 0.9414 | 0.9449 | OPEN LINE FROM BUS 549984 [BROOKLINE 7345.00] TO BUS 300045 [7MORGAN 345.00] CKT 1
547480 MON383 5 161.00 | 0.9415 | 0.9449 | OPEN LINE FROM BUS 549984 [BROOKLINE 7345.00] TO BUS 300045 [7MORGAN 345.00] CKT 1
640063 AURORA_7 115.00 | 1.0508 | 1.0413 | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1
640109 CHADRON7 115.00 | 1.0503 | 1.0307 | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1
640161 ELMCRK_7 115.00 | 1.0509 | 1.0352 | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1
640250 KEARNEY7 115.00 | 1.0505 | 1.0354 | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1
640259 LOUPCTY7 115.00 | 1.0518 | 1.0454 | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1
640269 MCCOOK 7 115.00 | 1.0525 | 1.0374 | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1
640326 REDWILO7 115.00 | 1.052 | 1.0371 | OPEN LINE FROM BUS 640184 [GENTLMN4 230.00] TO BUS 640010 [GENTLM1G 23.000] CKT 1
640405 WAYSIDE7 115.00 | 1.058 | 1.0389 | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1
645740 S3740 3 345.00 | 1.0529 | 1.0313 | OPEN LINE FROM BUS 645455 [S3455 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1
659818 COVALT 7 115.00 | 1.0501 | 1.0396 | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1

## SERC_N-1_VOLTAGE_WINTER
BUS | VCONT | VINIT | CONTINGENCY
300074 5CUBA3 161.00 | 0.9404 | 0.9707 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300077 5FLETCH 161.00 | 0.9421 | 0.9971 | OPEN LINE FROM BUS 300040 [7FLETCH 345.00] TO BUS 300077 [5FLETCH 161.00] TO BUS 300175 [1FLTCHTR 13.800] CKT 1
300094 5LOCUST 161.00 | 0.9408 | 0.9622 | OPEN LINE FROM BUS 300039 [7FAIRPT 345.00] TO BUS 300076 [5FAIRPT 161.00] CKT 3
300112 5SALEM 161.00 | 0.9484 | 0.9963 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300119 5SULLVN 161.00 | 0.9436 | 0.9673 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300142 4SULVN 138.00 | 0.9447 | 0.9668 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
300794 5LAMAR 161.00 | 0.9453 | 0.9947 | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1
300858 5SMRSVLEST 161.00 | 0.9435 | 0.9715 | OPEN LINE FROM BUS 300040 [7FLETCH 345.00] TO BUS 300077 [5FLETCH 161.00] TO BUS 300175 [1FLTCHTR 13.800] CKT 1
300950 5JASPER 161.00 | 0.9456 | 1.0082 | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1
301136 5BOURBN 161.00 | 0.9426 | 0.9681 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
301149 5STEELV 161.00 | 0.942 | 0.9785 | OPEN LINE FROM BUS 300047 [7SALEM 345.00] TO BUS 300112 [5SALEM 161.00] CKT 1
304370 3SO PINES 115.00 | 0.947 | 0.9731 | OPEN LINE FROM BUS 304360 [6WEST END SU230.00] TO BUS 305046 [6E11-ELLERBE230.00] CKT 1
304372 3CNTR PRK TA115.00 | 0.947 | 0.9732 | OPEN LINE FROM BUS 304360 [6WEST END SU230.00] TO BUS 305046 [6E11-ELLERBE230.00] CKT 1
304400 8RICH REACTO500.00 | 1.0889 | 1.0448 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
304413 3RAEFORD NOR115.00 | 0.937 | 0.9513 | OPEN LINE FROM BUS 304378 [6RICHMON230T230.00] TO BUS 304415 [6RAEFORD230T230.00] CKT 1
304414 3RAEFORD TAP115.00 | 0.9489 | 0.963 | OPEN LINE FROM BUS 304378 [6RICHMON230T230.00] TO BUS 304415 [6RAEFORD230T230.00] CKT 1
304752 3MAGGIE V SU115.00 | 0.9488 | 0.9672 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
305091 3E10-ARABIA 115.00 | 0.9439 | 0.9581 | OPEN LINE FROM BUS 304378 [6RICHMON230T230.00] TO BUS 304415 [6RAEFORD230T230.00] CKT 1
305095 3E10-RAEFORD115.00 | 0.9393 | 0.9536 | OPEN LINE FROM BUS 304378 [6RICHMON230T230.00] TO BUS 304415 [6RAEFORD230T230.00] CKT 1
305098 3E10-ROCKFIS115.00 | 0.9228 | 0.9374 | OPEN LINE FROM BUS 304378 [6RICHMON230T230.00] TO BUS 304415 [6RAEFORD230T230.00] CKT 1
306008 8OCONEE 500.00 | 1.0659 | 1.061 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306009 ANDERSON 100.00 | 1.0592 | 1.0582 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306012 IND 306012 100.00 | 1.0532 | 1.0522 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306017 CENTRAL 100.00 | 1.0528 | 1.0504 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306025 IND 306025 100.00 | 1.0576 | 1.0565 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306027 BUS 306027 100.00 | 1.0592 | 1.0582 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306031 BUS 306031 100.00 | 1.054 | 1.0529 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306048 IND 306048 100.00 | 1.059 | 1.058 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306049 IND 306049 100.00 | 1.058 | 1.058 | BASE CASE
306050 IND 306050 100.00 | 1.0589 | 1.0578 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306051 IND 306051 100.00 | 1.0591 | 1.0581 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306067 IND 306067 100.00 | 1.0527 | 1.0516 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306068 BUS 306068 100.00 | 1.0527 | 1.0517 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306070 BUS 306070 100.00 | 1.0528 | 1.0517 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306112 8BAD CRK 500.00 | 1.067 | 1.0641 | OPEN LINE FROM BUS 306113 [8JOCASSE 500.00] TO BUS 307690 [6JOCASSE BK 230.00] CKT 1
306113 8JOCASSE 500.00 | 1.0666 | 1.0627 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306117 LIONMTN 100.00 | 0.9132 | 0.9289 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
306120 ASHVL HW 100.00 | 0.9255 | 0.9411 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
306163 HNDRSNVL 100.00 | 0.9288 | 0.9435 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
306164 HORSESHO 100.00 | 0.942 | 0.958 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
306171 UPWARDRD 100.00 | 0.9281 | 0.9431 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
306192 RICH MTN 100.00 | 0.921 | 0.9365 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
306288 IND 306288 100.00 | 1.0537 | 1.0527 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
306337 8NEWPORT 500.00 | 1.0738 | 1.0632 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
306385 NEWPORT 100.00 | 1.0526 | 1.0513 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
306494 SUGAR HL 100.00 | 0.9485 | 0.9811 | OPEN LINE FROM BUS 306440 [6MCDOWL2 230.00] TO BUS 309427 [1MCDOW 2 1.0000] CKT 2
306546 8MCGUIRE 500.00 | 1.0723 | 1.0693 | OPEN LINE FROM BUS 308788 [8CLFSDTAP 500.00] TO BUS 308789 [1CLFSDGEN 24.500] CKT 6
306719 8ANTIOCH 500.00 | 1.0759 | 1.0681 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309035 [8ROCKSPGRTRT500.00] CKT Z1
306726 BECKRDIT 100.00 | 1.0544 | 1.0519 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
306737 DAN RIV 100.00 | 1.0588 | 1.0568 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
306761 MEADOWGR 100.00 | 1.0566 | 1.0547 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
306764 MOTLEY 100.00 | 1.059 | 1.0572 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
306792 IND 306792 100.00 | 1.0532 | 1.0506 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
306793 IND 306793 100.00 | 1.0526 | 1.05 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
306800 BUS 306800 100.00 | 1.0529 | 1.0504 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
306801 BUS 306801 100.00 | 1.0532 | 1.0507 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
306836 8WOODLF 500.00 | 1.0771 | 1.0666 | OPEN LINE FROM BUS 306850 [8PL GRDN 500.00] TO BUS 309057 [8GODBEYRTRT 500.00] CKT Z1
306849 8PARKWOD 500.00 | 1.0615 | 1.0548 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 306836 [8WOODLF 500.00] CKT 1
306850 8PL GRDN 500.00 | 1.0652 | 1.0576 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 306836 [8WOODLF 500.00] CKT 1
308471 NIXRDTAP 100.00 | 0.9431 | 0.9431 | OPEN LINE FROM BUS 304463 [6NEW BERN WE230.00] TO BUS 305142 [6E16-FAIRFEL230.00] CKT 1
308472 NIXRDRET 100.00 | 0.9406 | 0.9406 | BASE CASE
308602 DNRVRGEN 100.00 | 1.0591 | 1.0572 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
308708 BUS 308708 100.00 | 1.0529 | 1.0504 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308710 BUS 308710 100.00 | 1.0529 | 1.0504 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
308788 8CLFSDTAP 500.00 | 1.0748 | 1.0705 | OPEN LINE FROM BUS 308788 [8CLFSDTAP 500.00] TO BUS 308789 [1CLFSDGEN 24.500] CKT 6
308955 IND 308955 100.00 | 1.0558 | 1.0539 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
309001 8ASBRTRT 500.00 | 1.0967 | 1.061 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309001 [8ASBRTRT 500.00] CKT Z1
309002 8KATRTRT 500.00 | 1.0659 | 1.061 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309003 8ASBRTR 500.00 | 1.0967 | 1.061 | OPEN LINE FROM BUS 306008 [8OCONEE 500.00] TO BUS 309001 [8ASBRTRT 500.00] CKT Z1
309004 ANDERCAP 100.00 | 1.0592 | 1.0582 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309011 8KATRTR 500.00 | 1.0659 | 1.061 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309025 8RICHMNRTRT 500.00 | 1.0738 | 1.0632 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
309035 8ROCKSPGRTRT500.00 | 1.0825 | 1.0693 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309035 [8ROCKSPGRTRT500.00] CKT Z1
309050 BECKRCAP 100.00 | 1.0544 | 1.0519 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
309057 8GODBEYRTRT 500.00 | 1.0834 | 1.0576 | OPEN LINE FROM BUS 306850 [8PL GRDN 500.00] TO BUS 309057 [8GODBEYRTRT 500.00] CKT Z1
309160 8S_MTNRTRT 500.00 | 1.0777 | 1.0693 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309160 [8S_MTNRTRT 500.00] CKT Z1
309161 8S_MTNRTR 500.00 | 1.0777 | 1.0693 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309160 [8S_MTNRTRT 500.00] CKT Z1
309162 8ROCKSPGRTR 500.00 | 1.0825 | 1.0693 | OPEN LINE FROM BUS 306546 [8MCGUIRE 500.00] TO BUS 309035 [8ROCKSPGRTRT500.00] CKT Z1
309163 8RICHMNRTR 500.00 | 1.0738 | 1.0632 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
309164 8GODBEYRTR 500.00 | 1.0834 | 1.0576 | OPEN LINE FROM BUS 306850 [8PL GRDN 500.00] TO BUS 309057 [8GODBEYRTRT 500.00] CKT Z1
309308 LIONMTN_2 100.00 | 0.9289 | 0.9289 | BASE CASE
309312 HNDRSNV2 100.00 | 0.9288 | 0.9435 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
309313 HORSES1&2 100.00 | 0.942 | 0.958 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
309348 SUGAR H2 100.00 | 0.9485 | 0.9811 | OPEN LINE FROM BUS 306440 [6MCDOWL2 230.00] TO BUS 309427 [1MCDOW 2 1.0000] CKT 2
309360 DANRVR 100.00 | 1.0588 | 1.0568 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
309362 MOTLEY2 100.00 | 1.059 | 1.0572 | OPEN LINE FROM BUS 306827 [6ERNEST1 230.00] TO BUS 308501 [6ROCKHMBL2 230.00] CKT Z2
309371 HORSE3&4 100.00 | 0.942 | 0.958 | OPEN LINE FROM BUS 304781 [6CANERV230 T230.00] TO BUS 242532 [05NAGEL 230.00] CKT 1
309501 CENT1 100.00 | 1.0528 | 1.0504 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309502 CENT2 100.00 | 1.0528 | 1.0504 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309503 CENT3 100.00 | 1.0528 | 1.0504 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309504 CENT4 100.00 | 1.0528 | 1.0504 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309505 BECK1 100.00 | 1.0544 | 1.0519 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
309506 BECK2 100.00 | 1.0544 | 1.0519 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
309507 BECK3 100.00 | 1.0544 | 1.0519 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
309508 BECK4 100.00 | 1.0544 | 1.0519 | OPEN LINE FROM BUS 304332 [6ASHEBOR230T230.00] TO BUS 306848 [6PL GRDN 230.00] CKT 1
309526 NEWP1 100.00 | 1.0526 | 1.0513 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
309527 NEWP2 100.00 | 1.0526 | 1.0513 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
309528 NEWP3 100.00 | 1.0526 | 1.0513 | OPEN LINE FROM BUS 304377 [8RICHMON500T500.00] TO BUS 304400 [8RICH REACTO500.00] CKT 1
309577 AND1 100.00 | 1.0592 | 1.0582 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309578 AND2 100.00 | 1.0592 | 1.0582 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
309580 AND4 100.00 | 1.0592 | 1.0582 | OPEN LINE FROM BUS 306112 [8BAD CRK 500.00] TO BUS 308513 [1BADCREEKAT11.0000] CKT 1
311688 6CARFOREST 230.00 | 0.9445 | 0.9445 | OPEN LINE FROM BUS 306536 [6BUCK 230.00] TO BUS 306713 [6BECKRDT 230.00] CKT 2
312717 6PERRY R 230.00 | 0.9354 | 0.9479 | OPEN LINE FROM BUS 311716 [6BUCKSVL 230.00] TO BUS 312717 [6PERRY R 230.00] CKT 1
312726 6REDBLUF 230.00 | 0.9344 | 0.9501 | OPEN LINE FROM BUS 312726 [6REDBLUF 230.00] TO BUS 312729 [6MARION 230.00] CKT 1
324047 4BLACKBRNCH 138.00 | 0.9467 | 1.0011 | OPEN LINE FROM BUS 324106 [7HARDIN 345.00] TO BUS 324261 [4HARDN 138.00] CKT 1
324072 8PINEVL 500.00 | 1.0668 | 1.0589 | OPEN LINE FROM BUS 324072 [8PINEVL 500.00] TO BUS 324073 [8POCKETN 500.00] CKT 1
324073 8POCKETN 500.00 | 1.0573 | 1.0542 | OPEN LINE FROM BUS 360097 [8VOLUNTEER 500.00] TO BUS 360102 [8PHIPPS B NP500.00] CKT 1
324272 4LEITCHF 138.00 | 0.9387 | 0.9567 | OPEN LINE FROM BUS 324106 [7HARDIN 345.00] TO BUS 324261 [4HARDN 138.00] CKT 1
324308 4SHREWSB 138.00 | 0.9401 | 0.9568 | OPEN LINE FROM BUS 324106 [7HARDIN 345.00] TO BUS 324261 [4HARDN 138.00] CKT 1
324800 4MERE TVA 138.00 | 0.9355 | 0.951 | OPEN LINE FROM BUS 324106 [7HARDIN 345.00] TO BUS 324261 [4HARDN 138.00] CKT 1
360024 5FREEPORT TN161.00 | 1.0578 | 1.0534 | OPEN LINE FROM BUS 360024 [5FREEPORT TN161.00] TO BUS 360725 [5FREEPORT #2161.00] CKT Z1
360026 5CORDOVA #1 161.00 | 1.0655 | 1.0507 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
360027 5CORDOVA #2 161.00 | 1.056 | 1.0542 | OPEN LINE FROM BUS 360027 [5CORDOVA #2 161.00] TO BUS 365920 [5 MCCORD 8 161.00] CKT 1
360039 5JVILLE FP#2161.00 | 1.0543 | 1.0488 | OPEN LINE FROM BUS 360138 [5PARIS TN 161.00] TO BUS 361200 [5BIG SANDY T161.00] CKT 1
360049 5DAVIDSON #1161.00 | 1.052 | 1.0409 | OPEN LINE FROM BUS 360049 [5DAVIDSON #1161.00] TO BUS 361749 [5DAVIDSONSVC161.00] CKT Z1
360058 8E POINT AL 500.00 | 1.0597 | 1.0522 | OPEN LINE FROM BUS 360058 [8E POINT AL 500.00] TO BUS 360059 [5E POINT AL 161.00] CKT 1
360065 8WID CRK FP 500.00 | 1.0552 | 1.0516 | OPEN LINE FROM BUS 360065 [8WID CRK FP 500.00] TO BUS 360081 [8SEQUOYAH NP500.00] CKT 1
360079 8RACCOON MTN500.00 | 1.0566 | 1.0478 | OPEN LINE FROM BUS 360079 [8RACCOON MTN500.00] TO BUS 360664 [5RACCOON MT2161.00] CKT 5
360161 5OAKLAND TN 161.00 | 1.0561 | 1.0436 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
360162 5ROSSVILL TN161.00 | 1.0538 | 1.0436 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
360163 5DANCYVILLE 161.00 | 1.0544 | 1.0463 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
360317 5HUSTBURG TN161.00 | 1.0529 | 1.0475 | OPEN LINE FROM BUS 360138 [5PARIS TN 161.00] TO BUS 361200 [5BIG SANDY T161.00] CKT 1
360474 5BIG SANDY 161.00 | 1.0539 | 1.0389 | OPEN LINE FROM BUS 360138 [5PARIS TN 161.00] TO BUS 361200 [5BIG SANDY T161.00] CKT 1
360503 5MITCH CRNR 161.00 | 1.0546 | 1.0465 | OPEN LINE FROM BUS 360213 [5MILLER MS 161.00] TO BUS 361227 [5MITCH CRN T161.00] CKT 1
360504 5MOSCOW TN 161.00 | 1.0529 | 1.0421 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
360640 5JVILLE FP#3161.00 | 1.0641 | 1.0488 | OPEN LINE FROM BUS 360039 [5JVILLE FP#2161.00] TO BUS 360640 [5JVILLE FP#3161.00] CKT Z1
360643 5JVILLE CT#3161.00 | 1.064 | 1.0487 | OPEN LINE FROM BUS 360039 [5JVILLE FP#2161.00] TO BUS 360640 [5JVILLE FP#3161.00] CKT Z1
360724 5FREEPORT #1161.00 | 1.0578 | 1.0534 | OPEN LINE FROM BUS 360024 [5FREEPORT TN161.00] TO BUS 360725 [5FREEPORT #2161.00] CKT Z1
360725 5FREEPORT #2161.00 | 1.0565 | 1.0534 | OPEN LINE FROM BUS 360024 [5FREEPORT TN161.00] TO BUS 360724 [5FREEPORT #1161.00] CKT Z1
360726 5CORDOVA #1M161.00 | 1.0531 | 1.0507 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360727 [5CORDOVA #1T161.00] CKT Z1
360727 5CORDOVA #1T161.00 | 1.0655 | 1.0507 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361025 5HUSTBURG TP161.00 | 1.0529 | 1.0475 | OPEN LINE FROM BUS 360138 [5PARIS TN 161.00] TO BUS 361200 [5BIG SANDY T161.00] CKT 1
361089 5OAKLANDTN T161.00 | 1.0566 | 1.0441 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361091 5DANCYVILLET161.00 | 1.0544 | 1.0463 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361099 5BLAIR RD TP161.00 | 0.8914 | 1.035 | OPEN LINE FROM BUS 361099 [5BLAIR RD TP161.00] TO BUS 361383 [5W OAK RIDGT161.00] CKT 1
361146 5BLAIR RD TN161.00 | 0.7722 | 1.0348 | OPEN LINE FROM BUS 360692 [5ROANE B#2 161.00] TO BUS 361383 [5W OAK RIDGT161.00] CKT 1
361158 5MURPHY#2 NC161.00 | 0.9288 | 1.0228 | OPEN LINE FROM BUS 360423 [5HIWASSEE HP161.00] TO BUS 361158 [5MURPHY#2 NC161.00] CKT 2
361200 5BIG SANDY T161.00 | 1.0547 | 1.0397 | OPEN LINE FROM BUS 360138 [5PARIS TN 161.00] TO BUS 361200 [5BIG SANDY T161.00] CKT 1
361227 5MITCH CRN T161.00 | 1.0547 | 1.0465 | OPEN LINE FROM BUS 360213 [5MILLER MS 161.00] TO BUS 361227 [5MITCH CRN T161.00] CKT 1
361228 5MOSCOW TN T161.00 | 1.0534 | 1.0426 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361269 5CANADAVL TN161.00 | 1.0596 | 1.0466 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361383 5W OAK RIDGT161.00 | 0.7724 | 1.0351 | OPEN LINE FROM BUS 360692 [5ROANE B#2 161.00] TO BUS 361383 [5W OAK RIDGT161.00] CKT 1
361395 5HICK WITHE 161.00 | 1.0604 | 1.0484 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361400 5LONGTOWN TP161.00 | 1.0579 | 1.0477 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361401 5LONGTOWN TN161.00 | 1.0579 | 1.0476 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361465 5GALLAWAY TN161.00 | 1.06 | 1.048 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361492 5W PLSNT HLT161.00 | 1.0549 | 1.0471 | OPEN LINE FROM BUS 361227 [5MITCH CRN T161.00] TO BUS 361492 [5W PLSNT HLT161.00] CKT 1
361493 5W PLSNT HL 161.00 | 1.0547 | 1.0469 | OPEN LINE FROM BUS 361227 [5MITCH CRN T161.00] TO BUS 361492 [5W PLSNT HLT161.00] CKT 1
361568 5W SOMERVLE 161.00 | 1.0543 | 1.0425 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
361795 5PIPERTON TN161.00 | 1.0534 | 1.0436 | OPEN LINE FROM BUS 360026 [5CORDOVA #1 161.00] TO BUS 360726 [5CORDOVA #1M161.00] CKT Z1
365578 5HOLMES RD47161.00 | 1.0557 | 1.0527 | OPEN LINE FROM BUS 360024 [5FREEPORT TN161.00] TO BUS 360724 [5FREEPORT #1161.00] CKT Z1
365825 5POPL EST 77161.00 | 1.0536 | 1.0484 | OPEN LINE FROM BUS 365598 [5SE GATE 34 161.00] TO BUS 365825 [5POPL EST 77161.00] CKT 1
365829 5PIDGEON 82 161.00 | 1.0532 | 1.0455 | OPEN LINE FROM BUS 360174 [5ALLEN FP 161.00] TO BUS 365829 [5PIDGEON 82 161.00] CKT 1
365920 5 MCCORD 8 161.00 | 1.055 | 1.0486 | OPEN LINE FROM BUS 365591 [5NE GATE 33 161.00] TO BUS 365920 [5 MCCORD 8 161.00] CKT 1
380015 8THALMANN 500.00 | 1.0547 | 1.0432 | OPEN LINE FROM BUS 380009 [8W MCINTOSH 500.00] TO BUS 382158 [8MCCALL RD 500.00] CKT 1
382045 3LICK CREEK 115.00 | 0.9001 | 0.9613 | OPEN LINE FROM BUS 380147 [6BRANCH 230.00] TO BUS 382054 [6EATONTON C 230.00] CKT 1
382046 3LAKE OCONEE115.00 | 0.8914 | 0.9532 | OPEN LINE FROM BUS 380147 [6BRANCH 230.00] TO BUS 382054 [6EATONTON C 230.00] CKT 1
382158 8MCCALL RD 500.00 | 1.0695 | 1.0331 | OPEN LINE FROM BUS 380009 [8W MCINTOSH 500.00] TO BUS 382158 [8MCCALL RD 500.00] CKT 1
382329 3HARMONY J 115.00 | 0.9141 | 0.9744 | OPEN LINE FROM BUS 380147 [6BRANCH 230.00] TO BUS 382054 [6EATONTON C 230.00] CKT 1
382330 3HARMONY RD 115.00 | 0.9122 | 0.9725 | OPEN LINE FROM BUS 380147 [6BRANCH 230.00] TO BUS 382054 [6EATONTON C 230.00] CKT 1
382453 3YORKVILLE 115.00 | 0.9424 | 0.9671 | OPEN LINE FROM BUS 380183 [6CEDARTOWN 230.00] TO BUS 382439 [6CEDAR HILL 230.00] CKT 1
382804 6AL-GA LINE 230.00 | 1.0538 | 1.0369 | OPEN LINE FROM BUS 380179 [6ROOPVILLE 230.00] TO BUS 382804 [6AL-GA LINE 230.00] CKT 1
384375 8S.BESS 8 500.00 | 1.0521 | 1.0445 | OPEN LINE FROM BUS 384374 [6S.BESS 6 230.00] TO BUS 384375 [8S.BESS 8 500.00] CKT 1
384512 8SNOWDN8 500.00 | 1.0527 | 1.0462 | OPEN LINE FROM BUS 384511 [6SNOWDN6 230.00] TO BUS 384512 [8SNOWDN8 500.00] CKT 1
385312 8CLAY 8 500.00 | 1.0523 | 1.0486 | OPEN LINE FROM BUS 384234 [6CLAY 6 230.00] TO BUS 385312 [8CLAY 8 500.00] CKT 1
388700 8DANIEL8 500.00 | 1.0748 | 1.0323 | OPEN LINE FROM BUS 388700 [8DANIEL8 500.00] TO BUS 388702 [6DANIEL6 230.00] CKT 1

## FRCC_N-1_VOLTAGE_WINTER
BUS | VCONT pu | VINIT pu | CONTINGENCY
400005 FLACITY 230.00 | 1.065 | 1.0452 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400274 CORBETT 500.00 | 1.0529 | 1.0432 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400275 MARTIN 500.00 | 1.0612 | 1.0487 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400276 MIDWAY 500.00 | 1.0648 | 1.0381 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400289 ALLIGATR 138.00 | 0.9453 | 1.0033 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400292 BONI SPG 138.00 | 0.9439 | 1.0005 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400294 CAPRI 138.00 | 0.9398 | 0.9993 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400298 COCOPLUM 138.00 | 0.9198 | 1.001 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400304 ENGLEWOD 138.00 | 0.8939 | 0.9999 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400319 MYAKKA 138.00 | 0.8874 | 1.0018 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400320 NAPLES 138.00 | 0.9486 | 1.0064 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400324 P.RIDGE 138.00 | 0.947 | 1.0043 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400331 S VENICE 138.00 | 0.9353 | 1.0022 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400339 ROTONDA 138.00 | 0.8775 | 0.9931 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400343 COLLIER 230.00 | 0.9398 | 0.9945 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400345 GRANADA 230.00 | 0.8054 | 0.9815 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400350 MYAKKA 230.00 | 0.8149 | 0.9741 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400354 ORANGE R 500.00 | 1.0519 | 1.027 | OPEN LINE FROM BUS 400351 [ORANGE R 230.00] TO BUS 400354 [ORANGE R 500.00] CKT 1
400375 BALDWIN 115.00 | 0.9467 | 0.9953 | OPEN LINE FROM BUS 400458 [BALDWIN 230.00] TO BUS 400463 [DUVAL 230.00] CKT 1
400406 MACLENNY 115.00 | 0.9483 | 0.9928 | OPEN LINE FROM BUS 400458 [BALDWIN 230.00] TO BUS 400375 [BALDWIN 115.00] CKT 1
400476 POINSETT 500.00 | 1.0781 | 1.0502 | OPEN LINE FROM BUS 400467 [POINSETT 230.00] TO BUS 400476 [POINSETT 500.00] CKT 1
400484 ROBERTS 500.00 | 1.0556 | 1.035 | OPEN LINE FROM BUS 400484 [ROBERTS 500.00] TO BUS 400501 [ROBERTS 230.00] CKT 1
400492 TERRY 230.00 | 0.938 | 0.9928 | OPEN LINE FROM BUS 400351 [ORANGE R 230.00] TO BUS 400609 [GATEWAY 230.00] CKT 1
400501 ROBERTS 230.00 | 1.0827 | 1.0438 | OPEN LINE FROM BUS 400468 [PUTNAM 230.00] TO BUS 400501 [ROBERTS 230.00] CKT 1
400543 BELMEAD 138.00 | 0.9398 | 0.9994 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400552 AUBURN 230.00 | 0.8009 | 0.9881 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400559 FRANKLIN 138.00 | 0.9438 | 1.0057 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
400564 RATLSNAK 138.00 | 0.9389 | 0.9981 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400586 IMPERIAL 138.00 | 0.9481 | 1.004 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400609 GATEWAY 230.00 | 0.9322 | 1.0167 | OPEN LINE FROM BUS 400351 [ORANGE R 230.00] TO BUS 400609 [GATEWAY 230.00] CKT 1
400625 VANDRBLT 230.00 | 0.9372 | 0.9911 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400668 HOMELAND 230.00 | 0.9488 | 1.0051 | OPEN LINE FROM BUS 400268 [RANCH 230.00] TO BUS 400668 [HOMELAND 230.00] CKT 1
400732 MCGREGOR 230.00 | 1.065 | 1.043 | OPEN LINE FROM BUS 400119 [TURKEY P 230.00] TO BUS 400732 [MCGREGOR 230.00] CKT 1
400750 ALICO 230.00 | 0.9473 | 0.9985 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400758 SAN CARL 230.00 | 0.9474 | 0.9985 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400759 LIVNGSTN 230.00 | 0.9398 | 0.9945 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400818 CORTEZ 230.00 | 0.9309 | 0.9939 | OPEN LINE FROM BUS 400346 [JOHNSON 230.00] TO BUS 400818 [CORTEZ 230.00] CKT 1
400919 ORNGTREE 230.00 | 0.9379 | 0.991 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
400991 MAR1COLL 500.00 | 1.0612 | 1.0487 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
400992 MAR2COLL 500.00 | 1.0612 | 1.0487 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
401009 COAST 230.00 | 0.9348 | 0.9904 | OPEN LINE FROM BUS 401007 [PEACHLND 230.00] TO BUS 401009 [COAST 230.00] CKT 1
401038 GOLD_GTE 230.00 | 0.937 | 0.9912 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
401053 MCCALL 138.00 | 0.8794 | 0.9947 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
401059 TERRYDS 230.00 | 0.9381 | 0.9927 | OPEN LINE FROM BUS 400351 [ORANGE R 230.00] TO BUS 400609 [GATEWAY 230.00] CKT 1
401135 LRLWDISTTP 230.00 | 0.802 | 0.9941 | OPEN LINE FROM BUS 400348 [LAURELWD 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
401331 WC2 AUX1 500.00 | 1.053 | 1.0433 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
401332 WC2 AUX2 500.00 | 1.053 | 1.0433 | OPEN LINE FROM BUS 400266 [MIDWAY 230.00] TO BUS 400276 [MIDWAY 500.00] CKT 1
401351 MCCALLTP 138.00 | 0.8819 | 0.9969 | OPEN LINE FROM BUS 400552 [AUBURN 230.00] TO BUS 401135 [LRLWDISTTP 230.00] CKT 1
401709 SUMMIT 230.00 | 0.9369 | 0.9909 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
402583 MEADOW WD S 230.00 | 0.9204 | 0.9969 | OPEN LINE FROM BUS 402583 [MEADOW WD S 230.00] TO BUS 405704 [TAFT 230.00] CKT 1
402587 SKY LAKE 230.00 | 0.9374 | 0.983 | OPEN LINE FROM BUS 402587 [SKY LAKE 230.00] TO BUS 405701 [SO WOOD 230.00] CKT 1
402863 LK BRANCH 115.00 | 0.9478 | 1.0092 | OPEN LINE FROM BUS 402881 [FT MEADE 230.00] TO BUS 402894 [SOUTH POLK 230.00] CKT 1
402880 FISHEATINGCK230.00 | 0.8808 | 1.0062 | OPEN LINE FROM BUS 402877 [AVON PARK 230.00] TO BUS 402880 [FISHEATINGCK230.00] CKT 1
402884 KATHLEEN 230.00 | 0.9465 | 0.9953 | OPEN LINE FROM BUS 402271 [GRIFFIN 230.00] TO BUS 402884 [KATHLEEN 230.00] CKT 1
403098 OCCIDENT1 TP115.00 | 0.9229 | 0.9676 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403120 OCCIDENT2 TP115.00 | 0.923 | 0.9678 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403122 OCCIDENTAL1 115.00 | 0.9228 | 0.9675 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403123 OCCIDENTAL2 115.00 | 0.923 | 0.9678 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403124 OCCIDENTAL3 115.00 | 0.9235 | 0.9683 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403125 OCCIDENT3 TP115.00 | 0.9236 | 0.9683 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403126 OCCIDENTALCG115.00 | 0.9238 | 0.9685 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403127 OCCIDENTLMTR115.00 | 0.923 | 0.9678 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403139 WHITE SPRNGS115.00 | 0.9409 | 0.9841 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403140 WHITESPGS TP115.00 | 0.9411 | 0.9843 | OPEN LINE FROM BUS 403168 [SUWANNEE PKR230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 31
403145 WAUKEENAH TP115.00 | 0.9406 | 0.9936 | OPEN LINE FROM BUS 403167 [PERRY 230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 1
403146 WAUKEENAH 115.00 | 0.9405 | 0.9936 | OPEN LINE FROM BUS 403167 [PERRY 230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 1
403147 STAUGUSTN TP115.00 | 0.9346 | 0.988 | OPEN LINE FROM BUS 403167 [PERRY 230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 1
403170 WILCOX 230.00 | 0.9176 | 0.9943 | OPEN LINE FROM BUS 403165 [NEWBERRY 230.00] TO BUS 403170 [WILCOX 230.00] CKT 1
403799 OVERSTREETTP115.00 | 0.7999 | 0.991 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
403816 ZEPHYRHLLS N115.00 | 0.8 | 1.0233 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
403817 NEW RIVER 115.00 | 0.8049 | 0.9844 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
403835 NEW RIVER 230.00 | 0.9383 | 0.9831 | OPEN LINE FROM BUS 402271 [GRIFFIN 230.00] TO BUS 402884 [KATHLEEN 230.00] CKT 1
403838 ZEPHYRHLLS N230.00 | 0.9398 | 0.9851 | OPEN LINE FROM BUS 402271 [GRIFFIN 230.00] TO BUS 402884 [KATHLEEN 230.00] CKT 1
405700 PINEHILL 230.00 | 0.9479 | 0.9876 | OPEN LINE FROM BUS 402168 [WOODSMERE 230.00] TO BUS 405700 [PINEHILL 230.00] CKT 1
406671 BLCK_S_115 115.00 | 1.07 | 1.0388 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406699 MIDDLBR. 115.00 | 1.0675 | 1.0363 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406703 RDGWD TP 115.00 | 1.0665 | 1.0352 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406704 RIDGWOOD 115.00 | 1.0671 | 1.0358 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406705 RDGWD SW 115.00 | 1.0671 | 1.0358 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406715 WESCNTT. 115.00 | 1.0654 | 1.0341 | OPEN LINE FROM BUS 406673 [BLCK_S_230 230.00] TO BUS 406750 [BLCK_N_230 230.00] CKT Z1
406716 WORTHNTN 115.00 | 0.9489 | 0.9775 | OPEN LINE FROM BUS 400458 [BALDWIN 230.00] TO BUS 400463 [DUVAL 230.00] CKT 1
407024 CHAIRES 115.00 | 0.9287 | 0.9824 | OPEN LINE FROM BUS 403167 [PERRY 230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 1
407061 ST.AUGUS 115.00 | 0.9346 | 0.988 | OPEN LINE FROM BUS 403167 [PERRY 230.00] TO BUS 403169 [SUWANNEE RV 230.00] CKT 1
407098 ELAM 115.00 | 0.7947 | 0.9868 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
407100 ELAM TP 115.00 | 0.7964 | 0.9882 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
407113 OVERSTREET 115.00 | 0.7999 | 0.991 | OPEN LINE FROM BUS 403838 [ZEPHYRHLLS N230.00] TO BUS 403816 [ZEPHYRHLLS N115.00] CKT 1
407431 STC EAST 230.00 | 0.938 | 1.0101 | OPEN LINE FROM BUS 402882 [HOLOPAW 1 230.00] TO BUS 407431 [STC EAST 230.00] CKT 1
407432 STC SOU 230.00 | 0.9372 | 1.0054 | OPEN LINE FROM BUS 402882 [HOLOPAW 1 230.00] TO BUS 407431 [STC EAST 230.00] CKT 1
408301 GANNON-RX230230.00 | 1.0522 | 1.0522 | BASE CASE BASE CASE
408700 GANNON 230.00 | 1.0522 | 1.0522 | BASE CASE BASE CASE
409803 BRNT STR 138.00 | 0.9355 | 1.0046 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409807 SO CAPE 138.00 | 0.9176 | 0.988 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409808 CARNSTN 138.00 | 0.9447 | 0.9931 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
409810 CP CORAL 138.00 | 0.9108 | 0.9818 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409811 DEL PRDO 138.00 | 0.9207 | 0.9909 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409813 IMOKALEE 138.00 | 0.9474 | 0.9954 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
409814 INDUS TP 138.00 | 0.9248 | 0.9947 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409820 MARCO IS 138.00 | 0.9362 | 0.9959 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
409821 F SMITH 138.00 | 0.9345 | 0.9943 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
409824 PN ISL 138.00 | 0.916 | 0.9868 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409826 SANIBEL 138.00 | 0.9085 | 0.9798 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409829 CP CL TP 138.00 | 0.9153 | 0.986 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409830 SO CP TP 138.00 | 0.9108 | 0.9818 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409831 DEL PRTP 138.00 | 0.9247 | 0.9946 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409832 INDUSTRL 138.00 | 0.9247 | 0.9946 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409835 WEST CC 138.00 | 0.9257 | 0.9956 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409838 AGUALINDA 138.00 | 0.9218 | 0.992 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409839 NO CAPE 230.00 | 0.938 | 1.003 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409840 NO CAPE 138.00 | 0.9356 | 1.0047 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409850 AMU SOUTH 138.00 | 0.9461 | 0.9941 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
409851 TRAFALGAR 138.00 | 0.9338 | 1.003 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409860 IMMOKALEE W 138.00 | 0.9487 | 0.9966 | OPEN LINE FROM BUS 400344 [FT MYERS 230.00] TO BUS 401348 [FM2A CTS 230.00] CKT 1
409863 KISMET 138.00 | 0.938 | 1.003 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1
409865 KISMET TP 138.00 | 0.938 | 1.003 | OPEN LINE FROM BUS 409816 [LEE 230.00] TO BUS 409839 [NO CAPE 230.00] CKT 1